# SPEAR3 RF System Upgrade

# SSRL Advances the Science Mission

(A short summary of SSRL’s impact on science)

SSRL enables and supports outstanding scientific research by a broad user community in a safe environment. SSRL operates approximately 9 months each year with a very high reliability -- delivering more than 97% of scheduled x-ray beam time. Experiments conducted at SSRL resulted in over 18,000 scientific publications since 1974, with 20% in high-impact journals.

# Challenge to maintain SSRL Science Capabilities

(A short summary for the operation challenge with the current rf system)

Leveraging the RF technology and experts developed for PEPII project, the SSRL was successfully built and operated over the last few decades. However, the technology has been lacking of development and maintenance since the shutdown of PEPII almost 20 years ago, and the most of the experts are no longer at SLAC. Today, we are heavily relying on the few remaining experts for maintenance. To carry SSRL for the next 10+ years, we recognize the need for a stable and long-term solution for the SPEAR3 RF system.  Leveraging the current RF technology and experts developed in SLAC is considered the best approach.

To maintain the photon science capabilities of SSRL, it is essential that this world-class facility be well maintained and improved over the next 10+ years. After more than 20 years of operation, the SSRL storage ring presents a particular challenge, especially in terms of repairing its high-power RF system. The current RF system, developed with PEPII technology, utilizes a single 90 kVDC high voltage power supply (HVPS) and a single 1.5 MW klystron to power the four SPEAR3 avities.  It has been in use for almost 20 years.  SPEAR3 currently requires 800 kW of RF power for its 500 mA electron beam at 3 GeV.

The klystron and HVPS are single points of failure for SPEAR3.  The time required to replace or repair either of these devices is measured in days.  After the end of the PEPII project, we reduced the mean time to repair a failed HVPS by bringing in a retired PEPII HVPS to SPEAR3 as a “warm spare”.  This allows us to reduce the downtime due to a failed HVPS to the time it takes us to change over from the failed supply to the spare, typically one day shift of effort from four different working groups at SLAC.

We do not have the space to keep a “warm spare” klystron at SPEAR3.  Instead, our goal is to keep this tested spare in the SLAC Technology and Innovation Directorate’s (TID) Test Stand (TS) 18, where all of the PEPII and SPEAR3 klystrons were tested.Two klystrons, retired from PEPII, are awaiting testing at TS18 to be spares for SPEAR3’s RF system.  However, since the shutdown of PEPII, TS18 is not in normal operation and lacks maintenance.  The retired klystrons have also lacked maintenance and are not currently operational. (Blockages in cooling water circuitry prevent them from even being tested at high power.) Without any functional backup klystrons and test stand, the overall RF system is at high risk; a failure of the current klystron could result in a prolonged downtime.

When PEPII was operational, SLAC devoted multiple engineers and crews of technicians to the support and maintenance of the high-power klystrons and associated 90 HVPSs.  With the end of the PEPII project almost 20 years ago, these engineers and technicians moved on to other duties.  Most are no longer at SLAC.  The current system relies heavily on the few remaining experts for maintenance.

Once effort is devoted to restoring TS18 to operation it is likely that we will have two tested, spare klystrons.  But we will still need to develop a sustainable maintenance plan for our HVPSs.  We need to train new engineers and technicians on a highly specialized and complex system that only exists at SLAC so that they can support SPEAR3 after the current SLAC experts retire.

# Proposed SPEAR3 RF System Upgrade

(A short summary for the scope of the rf upgrade project)

Looking ahead to the next 10+ years, we recognize the need for a stable and long-term solution for the SPEAR3 RF system. With the impressive performance and maturity of solid-state amplifier (SSA) technology, SSAs are being widely deployed to replace klystrons in storage rings globally. One advantage of SSAs is that they do not require a complex, unique HVPS.  They operate from commercial 50 VDC power supplies.  Maintenance of the SSAs typically requires only replacement of failed modules with spare modules.  There is minimal technical training required to safely replace the modules.

SSAs are already in use at SLAC.  The SPEAR3 Injector ring has been successfully powered by an SSA for seven years.  LCLS-II is also powered by SSAs.  Therefore, there already exists a team of engineers and technicians at SLAC who are trained in the support and maintenance of SSAs.  That skill set will exist at SLAC at least as long as LCLS-II and LCLS-II HE operate.

We are currently upgrading our SPEAR3 RF system to modernize its low-level radio frequency (LLRF) components from an old, but high-performance, system running on obsolete custom hardware to a better high-performance system running on modern hardware.  This LLRF upgrade does not change the high-power elements, the klystron and HVPS, of our system.  As a follow on to the LLRF upgrade, we are proposing an upgrade project to replace the existing high-power components with an SSA-based high-power system. The scope of the project includes:

- A 1 MW capacity SSA RF system, with four 250 kW SSA stations to power the four SPEAR3 RF cavities separately.  This will give us some overhead above our current required 800 kW of operational power.

- An RF test station, including local RF source, machine protection system, circulator, and 250 kW load, to fully evaluate the performance and complete acceptance tests of the four SSA stations as they are delivered from the vendor.

- A 12.47 kVAC to 480 VAC 2.5 MVA transformer, with associated breaker and distribution panel for five each, 500 kW main panel breakers for the four production and one test SSA stations.

- Expand the existing commercial LLRF system to control the four SSAs and integrate them with other systems.

- Four each 250 kW circulators at 476 MHz.

- Reconfiguration of the high power waveguide system to the four cavities.

- Infrastructure improvements to accommodate the SSA stations and to provide the necessary electrical utilities described above and cooling water. We’ll retrofit the current space between the SPEAR3 klystron and storage ring to host the SSA stations. A new structure with an area of xxx sqt near the current RF station will be needed to host the power supply.

- These infrastructure upgrades must be made compatible with the existing high power klystron system powering SPEAR.  All SSA stations must pass the acceptance tests and be ready for operation.  During a major downtime, the waveguide system for the cavities will be reconfigured from one very large single RF source to four large RF sources.

This upgrade will not only reduce the likelihood of RF system failures but also simplify maintenance, resulting in significant budget savings for long-term operation.

# Cost and Timeline

The total project cost is estimated to be approximately $20 M, as detailed in Table 1. The project timeline is about five years from the approval date, as detailed in Table 2, with operations expected to begin in the 2030–2031 timeframe.

Table 1 The rough order of magnitude cost estimate

| Items | 4 250kW SSA | RF test station | 480 Power supply | LLRF | Infrastructure | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Cost in M$ |  |  |  |  |  |  |

Wild guesses at costs:

- SSA:  $10/W  $10M

- 480 VAC distribution system  $2-3M

- Conventional construction upgrade of space for SSAs  $3M (including LCW?)

- Circulators (4)  $0.2M - 0.6M  (cannot find cost of our circulator purchase in 2015 in procurement database.  Saw some old quotes for $35k for 64kW from 8 years ago.

- Additional LLRF chassis  $0.2M

- MPS system  $0.2-0.4M

- Waveguides  $0.1M

- Miscellaneous interface electronics $0.2M

Table 2 The estimated project timeline

| Items | RF design | SSA procurement and delivery | SSA installation and commissioning | Total |
| --- | --- | --- | --- | --- |
| Time (Months) | 6 | 48 | 6 | 60 |

Somewhere in here there should probably be a step that we evaluate the configuration of the 250 kW unit as a close to finished prototype and look for potential weaknesses such as thermal stresses.  That likely increases the design time, iterating with the vendor and the testing time.  I have loaded up the procurement and delivery, but it could go elsewhere.