TECHNICAL DESIGN EXTRACTION NOTE

PEP II RF Power Supply - Klystron Power Supply System Schematic

Drawing No.: SD-730-790-01-C1  |  SLAC / Stanford University

# 1. Document Identification

| Field | Value |
| --- | --- |
| Drawing Number | SD-730-790-01-C1 |
| Title | PEP II RF PWR SUPPLY - Klystron Power Supply Schematic |
| Organization | Stanford Linear Accelerator Center (SLAC) |
| Location | Stanford University, Stanford, California |
| Sheet | 1 of 1 |
| Engineer | R. Cassel (2/10/03) |
| Drafter | W. Corporon |
| Checker | J. Olszewski (2/19/03) |
| Approval | J. Olszewski |
| Revision | C1 |
| CAD File | SD-730-790-01-C1 |
| Drawing Class | System Schematic Diagram |

# 1.1 Revision History

| Rev | Description | Date |
| --- | --- | --- |
| C1 | Revised per engineering changes | 2003 |

# 2. System Overview

This schematic provides the top-level system architecture for the PEP II RF High Voltage Power Supply (HVPS) system. It shows the complete power conversion chain from 12.5KV 3-phase AC input to high-voltage DC output for klystron operation at -77KV, 27 amps.

# 3. Major Components and Assemblies

| Component | Rating / Description | Function |
| --- | --- | --- |
| Phase Shifting Transformer | 12.5KV 3-Phase input | Provides 30-degree phase shift for 12-pulse operation |
| Disconnect & Breaker | 12.5KV rated | Safety isolation and primary protection |
| Thyristor Controlled Rectifier | 40KV 80A | Phase-controlled rectification for voltage regulation |
| Rectifier Transformer | High-voltage isolation | Steps voltage up for rectification |
| Filter Rectifiers | 30KV rated | Rectification of AC to DC |
| Filter Capacitors | 8µFD 30KV | Output filtering and energy storage |
| Filter Inductor | High current rated | L-C filtering for ripple reduction |
| Termination Resistors | 500 ohm 1KW | Damping and cable matching |
| Crowbar Thyristor | 40KV 80A (60KV rated) | Fast-acting fault protection |
| Klystron Load | 50KV, 27 Amps | RF power tube load |

# 4. Power Conversion Architecture

## 4.1 Input Power System

Primary Input: 12.5KV 3-phase AC input feeds through a disconnect and breaker assembly for safety isolation. The phase shifting transformer provides dual secondary outputs with a 30-degree phase shift for 12-pulse rectifier operation.

## 4.2 Rectification System

The thyristor controlled rectifier section uses SCRs rated at 40KV 80A for phase-angle-controlled rectification. The 12-pulse configuration uses two 6-pulse rectifier sets fed from the phase-shifted transformer secondaries. This eliminates 5th and 7th harmonics and doubles the ripple frequency to 720Hz.

## 4.3 Filtering

The output filter section includes filter capacitors (8µFD, 30KV) and a filter inductor forming an L-C filter network. Filter resistors (500 ohm, 1KW) provide damping. The filtered output reaches -77KV DC.

# 5. Voltage Distribution

| Node | Voltage | Notes |
| --- | --- | --- |
| AC Input | 12.5KV 3-Phase | Primary input from facility power |
| Post Phase-Shift Transformer | ~26KV | Stepped/shifted voltage |
| Post SCR Rectifier | ~52KV | Phase-controlled rectified DC |
| Filter Output | -77KV DC | Filtered high-voltage DC output |
| Crowbar Rating | 60KV / 40KV 80A | Fault protection threshold |
| Termination | -98KV | Cable termination voltage |

# 6. Protection Systems

## 6.1 Crowbar Protection

A crowbar thyristor rated at 40KV 80A (with 60KV capability) provides fast-acting fault protection. When triggered, it short-circuits the output to divert fault energy away from the klystron load.

## 6.2 Primary Protection

The disconnect and breaker at the input provide primary isolation and overcurrent protection at the 12.5KV level.

# 7. Load Interface

The klystron load operates at 50KV with 27 amps current draw. The supply provides negative high voltage (-77KV) through a grounded system. The klystron is the RF power amplifier tube for the PEP II accelerator RF system.

# 8. Signal Flow

Signal flow (input to output):
1. 12.5KV 3-Phase AC Input
2. Disconnect & Breaker (safety isolation)
3. Phase Shifting Transformer (30° phase shift, dual secondary)
4. Thyristor Controlled Rectifier (40KV 80A, phase-angle control)
5. Rectifier Transformer (voltage step-up/isolation)
6. Filter Rectifiers (30KV rated)
7. Filter Inductor + Filter Capacitors (8µFD 30KV) + Termination (500Ω 1KW)
8. Output: -77KV DC to Klystron (50KV, 27A)
9. Crowbar Protection (40KV 80A) across output
10. GND reference

# 9. Design Notes

- 12-pulse configuration provides improved harmonic performance (eliminates 5th/7th harmonics)

- Ripple frequency is 720Hz (12 × 60Hz)

- System delivers approximately 2MW of power (77KV × 27A)

- Negative polarity output for klystron cathode operation

- Multiple protection layers: breaker, SCR control, crowbar

# 10. AI Replication Checklist

| # | Item | Key Parameters |
| --- | --- | --- |
| 1 | AC Input | 12.5KV 3-phase |
| 2 | Phase Shifting Transformer | 30° phase shift for 12-pulse |
| 3 | Thyristor Controlled Rectifier | 40KV 80A SCRs |
| 4 | Rectifier Transformer | HV isolation |
| 5 | Filter Rectifiers | 30KV rated |
| 6 | Filter Capacitors | 8µFD 30KV |
| 7 | Filter Inductor | LC filter |
| 8 | Termination | 500Ω 1KW |
| 9 | Crowbar | 40KV 80A thyristor |
| 10 | Output | -77KV DC, 27A to klystron |

END OF TECHNICAL DESIGN EXTRACTION NOTE – SD-730-790-01-C1