## MEETING NOTES

March 10, 2026

Attendees: Javier, Jim, Andi, Rob, Faya, Xiaobiao, Kira

1. LCW / HCW Cooling System Review

1.1 Existing System Background

Rob found Spear Engineering Note M535, which documents the original LCW system design.

The system piping was originally designed for 600 GPM (max), but has been operated at only 300 GPM.

The HCW (High Conductivity Water) system was installed specifically for the SPEAR/PEP2 RF system, as a local system that may not appear on facility master LCW drawings.

The existing HCW system for the magic loads (RF power dumps) is separate from the LCW system that cools the Klystron.

All Klystron cooling (collector, circulator, body circuits) uses LCW, not HCW.

Magic loads (RF power dumps on the tunnel roof) and circulator loads are cooled by HCW.

1.2 Current Klystron Cooling Flow Data

Klystron collector: approx. 150 GPM (per design document); actual flow may be 170-270 GPM -- needs verification with Eddie.

Klystron circulator: approx. 15 GPM.

Original Klystron heat load was specified at 1,300 kW; current operation is 800 kW nominal.

Current HCW MPS (Machine Protection System) limit: 75 degrees C; currently running at 25 degrees C.

Collector water delta T: 12 degrees C currently; MPS limit is 20 degrees.

1.3 update by Eddie 3/11/2026

SPEAR complex total LCW: 2,539 GPM (confirmed by Eddie). Breakdown: SPEAR ring 1,853 GPM / 2.4 MW, Injector Building 140 428 GPM / 160 kW, SSRL 258 GPM / 130 kW. Inlet temp 30.6 degrees C; SPEAR outlet 35.6 degrees C. Inlet pressure 255 psi, outlet pressure 31 psi. Combined thermal load ~2.69 MW.

Note: Engineering notes reviewed during the meeting are outdated -- the boost pump was removed ~2010 and a new SPEAR Klystron was installed ~2020, both of which changed operating parameters (per Eddie).

SPEAR ring LCW delta T (confirmed by Eddie): inlet 30.6 degrees C, outlet 35.6 degrees C (delta T = 5 degrees C). Total complex thermal load ~2.69 MW at 2,539 GPM total flow.

1.4 New SSA Cooling Requirements

4 new SSA stations are planned in the new building.

Each SSA station requires approximately 100 GPM of LCW.

Total LCW demand for all 4 SSA stations: approximately 400 GPM with deltaT~ 10K

An additional SSA module of 250 kW will be operated in parallel with the Klystron (for commissioning/acceptance testing as vendor delivers units sequentially).

SSAs need to run cooler than the Klystron, which is why the flow requirement per unit is higher.

The existing 4-inch LCW supply piping to the Klystron room is insufficient to handle 400-500 GPM; it would result in excessive velocity (12+ fps, vs. desired 8-9 fps max per Javier).

1.5 LCW Supply Options Discussed

Option A: Tap off the existing Klystron LCW header near Building 132 (near 507 sidewalk). Not feasible at full flow due to 4-inch pipe size limitation.

Option B: Run a new, larger connection (6-inch or larger) back to the main LCW distribution header upstream. This is technically feasible but requires more work.

Option C: Install a new dedicated LCW pumping station (cooling tower not needed). This would be a standalone system, avoiding disruption to existing operations and avoiding dependency on Facilities' system capacity.

Key constraint: The existing Klystron system must remain operational during any upgrade work. A 2-month summer shutdown window is available for plumbing modifications.

Action: Javier will organize a meeting with Ota (F&Ot) plus Rob and Andi to review LCW demand and evaluate connection options to the 1801 system.

1.6 Building 122 Test Lab LCW

Building 122 (test lab) has an existing LCW connection outside the building that still functions -- it feeds the high-voltage power supplies.

The flow required for the 122 test lab SSA is approximately 1/8 of the full 250 kW unit -- roughly 12-15 GPM for the SSA plus a comparable amount for the load.

2. New SSA Building Layout & Structure

2.1 Building Height & Clearance

Proposed new SSA building height: approximately 27 feet (matching Building 130 elevation).

Clear height under the equipment platform structure: 9 feet for now.

SSA rack unit height: approximately 6 feet 4 inches.

The upper structure/mezzanine framing depth: approximately 3 feet (may be reducible) for now.

Total platform height including upper structure: approximately 12 feet.

Javier noted it is easier to scale back the height later than to increase it.

2.2 Existing Obstructions to Remove

The metal siding on the existing building wall (adjacent to the new structure) will remain.

All equipment behind the siding in the construction zone must be removed, including cable trays running through this area.

There is an existing I-beam (crane beam) at approximately 86 inches from the floor at a certain location -- this constrains clearance and must be accounted for in the design.

There is an existing large pipe manifold protruding into the sidewalk adjacent to Building 132 that houses the Klystron LCW distribution -- this is an important tie-in point.

2.3 Pipe Relocation Option

An existing large pipe (approximately 3-4 feet from its current position) could be relocated at modest cost.

Benefit: Relocating the pipe would allow the new building footprint to be extended (longer), which could ease layout constraints.

This option is being kept open for consideration as the design develops.

2.4 Access & Stairway

Regular access to upper-level SSA equipment is required for operations, troubleshooting, and module swaps.

A ladder is not acceptable (safety precedent: a co-worker was hospitalized after a fall from a ladder at the high-voltage power supply building; a full OSHA-compliant stairway was subsequently required).

A proper stairway conforming to OSHA requirements must be included.

Javier estimated that at 15 feet height with 7-inch risers, approximately 25 risers are needed, which requires a landing.

Options discussed: incorporate a stairway at the end of 132, or extend the existing stairway with a catwalk to reach the upper level.

No final decision made; continue evaluating.

3. RF Waveguide Routing & SSA Layout

3.1 SSA Rack Orientation

Rob presented a plan view of the SSA station layout.

All waveguides must exit from one end of the building (the cavity side).

Waveguide Routing Details

Each SSA cabinet outputs via a 6-1/8 inch coaxial line.

8 coaxial lines feed into a WR2100 rectangular waveguide combiner, then output goes to the RF cavities.

The combining can be done at the level between racks (mid-height) or run coaxial lines vertically to combine above the racks -- this as an additional degree of freedom to reduce space conflicts.

Two waveguide runs pass through the tunnel roof to the RF cavities (one per cavity pair). Each requires its own penetration and routing.

Waveguide routing will need to avoid crossing each other and will require Unistrut hangers from the ceiling or structure, spaced approximately every 8 feet. WR2100 weighs approximately 10 lb/ft.

Lower waveguide runs can be also supported from the equipment platform structure above.

A circulator must be installed in each waveguide run between the SSA output and the cavity.

3.3 Waveguide Length Matching

The waveguide paths from the SSA building to the RF cavities must maintain approximately the same electrical phase. Physical lengths may therefore differ by integer multiples of the guide wavelength

Operating frequency: 476.3 MHz. Free-space wavelength is about 64.2cm, and the corresponding Waveguide wavelength is approximately 80.4 cm.

4. Electrical Infrastructure

4.1 Building 122 Test Lab Power

Andi: an F&O electrical engineer (Naomi) will help with electrical work for Building 122 test lab power. She is on vacation for the next 2 weeks but will begin working on the project upon return.

4.2 Building 118 Power Separation

Naomi will also support separating power circuits for two TSP racks in Building 118, as requested by Jim.

5 Key Decisions Made

9 feet clear height under the platform structure is agreed as the working target for the new SSA building.

LCW will cool the SSA racks directly (not HCW). HCW is reserved for the all loads.

A proper OSHA-compliant stairway (not a ladder) is required for upper-level access. Design to be resolved.

Plumbing modifications to the live Klystron system will be targeted for the 2-month summer downtime window.

## Meeting Notes 2/26/2026

Attendees: Jim, Andi, Ryan, Faya

Walk through building 122

- Andi to reach out regarding the engineering design of the electrical system.

- Ryan to coordinate with Casten Hast on relocating three spare cavities to ESA, and with PJ on rack cleanup.

- LCW options:

Tap off upstream or downstream of the existing pipes for the HVPS.

The upstream option requires less piping and is likely lower cost.

## Meeting Notes 2/24/2026

Attendees: Javier, Jim, Andi, Rob, Faya

Key Discussions:

1. Site Constraints & Building Extension Concept (Javier)

- Existing electrical alcove: ~477 sq ft.

- Proposed extension of Building adds ~636 sq ft + ~300 sq ft equipment platform → total usable space significantly increased.

- 5-ft aisle proposed for personnel egress; fire marshal approval required.

- Structural approach:

  - Option: Extend walls around existing pipes.

  - Remove non-structural shed walls and one minor column (new column + I-beam to replace roof load).

  - Crane beam and main structural columns remain untouched.

- Conclusion: Extension is feasible and preferred; two-story SSA layout now realistic.

2. Access, Egress & Future Coordination

- Future MIE beamline extension will occupy current roadway area and require utility relocations outside the ring — both SSA and MIE are 5+ years out but must be coordinated.

- Need to Remove old air-handler/chiller equipment behind 507 to open secondary access route around 117/118 – This will be part of the SSA upgrade project.

- 507 roll-up doors: Facilities may only need one; confirm with Boris/Diego.

3. Electrical & Transformer

- New 2.5–3 MW transformer preferred outdoor (dry-type or oil-filled) to avoid indoor fire-hazard classification and building protection costs.

- Conceptual location: The primary location is in the field near the SPEAR tunnel access entrance. A 12 kV feed will be routed from Building 507 to a transformer, stepped down to 480 V distribution, and then fed back to the SSA racks.

- Existing 502 substation timeline uncertain — do not rely on it.

- Two electrical Panels in alcove: relocating one on the right (Andi); the other can be moved.

4. RF Waveguide & Roof Work

- Need to straight the S-shaped Cable trays for 4 waveguide runs on roof.

- Vertical orientation of rf load/circulators is considered for space savings.

- Existing klystron-room control racks stays in place.

- Roof waveguide splitters removed; direct 1:1 SSA-to-cavity runs (4 independent).

- Cable trays between 118 and ring to be relocated ~10 ft outward for clearance.

- Existing 1.5 MW circulators (PEP spares) available; smaller 250 kW units optional.

5. Equipment Installation & Maintenance

- Large items (transformers, air handlers) require crane over ring road.

- New building to include roll-up door(s) for forklift/rack delivery.

- Maintain manhole and pit drainage access (rare use, but critical).

## Meeting Notes 2/11/2026

Attendees: Javier, Jim, Andi, Rob, Kira, Faya

Key Discussions:

- Electrical setup and power supply:

- Options: Use spare circuit breaker from Substation 507 or new setup. Avoid piggybacking on F&O project due to timeline delays.

- Transformer location: Proposed near condensing unit, but conflicts noted.

- Need 480V distribution panels for 4x 250kW SSA units (potentially 4-8 buckets per unit, Each unit includes 8 of 32 kW SSA blocks).

- Arc flash considerations: Aggressive breaker settings to reduce hazards.

- Spatial and structural constrains:

- Current room in Building 132 is too small for SSAs; expansion needed.

- Options:

- Single-floor extension: Extend building eastward ~22 ft wide x 50 ft deep from Klystron room wall. Measure clearances around chilled water lines, stairs, and 12kV manhole (need 3 ft around equipment).

- Mezzanine: Stack SSAs vertically (7 ft clearance per level + ~1 ft floor). Use existing 14 ft concrete wall height; add blocks if needed. Feasible but check with RP about 2nd layer access during operation.

- Infield extension: Build into infield for more space, but concerns about waveguide efficiency (extra length), vehicle access, and construction over operating Klystron (limited to 6-8 week summer downtime).

- Historical drawings reviewed for structural insights; upload to sharepoint for team access.

- Conflicts: HVAC condensing unit relocation (for BPM rooms; must meet code). Transformers, air handlers, MPS controls system in current space require relocation before construction.

- Preference: Single-floor if possible; mezzanine as backup. Avoid major disruptions to Klystron operations.

- Relocations and feasibility:

- Condensing unit: Small, outdoor-rated; can move 5-10 ft or to temporary shed. No flexibility in current plan, but SSA priority may override.

- Other equipment: Transformers (2-3), distribution panels, controls cabinets—relocatable during downtime. Air handler stays indoors but flexible.

- SSA Cooling, access and design:

- SSAs: 4 units; check heat to air (data sheet, most of heat will be removed by LCW. The total dissipation to air is about few tens of kW, likely no major HVAC needed), fan orientation (side-blowing possible), water manifold (bottom access).

- Waveguides: support ~10-50 lbs/ft; minimize distance to cavities for efficiency.

- Timeline and proposal:

- Rough timeline: cost by early May, full proposal by middle of June

- Report: formal proposal format include scope, risk, cost, timeline, major milestones.

Action items:

- Javier: site visit, measure spaces, upload drawings, and continue working on electrical diagram.

- Rob: refine SSA layout sketches, check clearances

- Jim: contact 2nd SSA vendor

- Faya: discuss report format with Xiaobiao, and refine timeline.

- All: access top area during next PAMM (2/23) for shielding, cable tray assessment.

## Meeting Notes 1/27/2026

Attendees: Faya, Rob, Andi, Javier, Kira

1. Power Infrastructure Upgrades (Substations 502 and 507)

- Power for the SSAs was discussed, with Substation 507 identified as the preferred option due to proximity and relatively shorter timeline compared to Substation 502.

- Substation 502 would require relocation to the infield, with an estimated timeline of 3–5+ years (2029–2032) and a cost of approximately $8–9M, funded through IGPP/GPP.

- Substation 507 would require relocating the existing transformer (currently near Building 118) to the backside of the substation to meet code clearance requirements. This option is estimated to take 2–3 years and cost $1–2M.

- The SSA installation requires a new 2.5–3 MVA transformer. Potential locations include the former 507 transformer pad (after relocation) or near the 507 breaker. Minimizing distance to reduce feeder length and cost is important.

- Javier has contacted F&O for additional details; Andi will coordinate as needed. Key items to confirm include available breaker capacity at Substation 507 and code compliance. Boris (F&O) expressed general support, though timelines remain uncertain.

2. Space Constraints and Building Modifications (Building 132)

- The existing space is approximately 12 feet wide, which is insufficient to accommodate 32 SSAs (32 kW each, ~1 MW total) while maintaining required access and code clearances.

- A vertical expansion approach was discussed as the most viable solution:

  - Extend the building outward and add a two-story structure or mezzanine.

  - Install SSAs on both the ground level and an upper level to preserve access to pits, roll-up doors, and utilities.

- Potential structural modifications include:

  - Removing siding and selected columns

  - Adding new columns and beams to meet seismic requirements

  - Installing roll-up doors for equipment handling

  - Providing crane access (a 2-ton crane was suggested)

  - Relocating existing equipment such as HVAC units, electrical panels, and MPS cabinets as needed

- Clearance of approximately 6–7 meters is required for a two-level SSA layout.

- Existing constraints include:

  - Maintaining access to a manhole/storm drain near Substation 507

  - Avoiding interference with crane-support columns

  - Preserving access to the pit beneath the room, including relocation of ladders as needed

- A purely horizontal layout is not feasible.

3. Timelines and Project Phasing

- The overall project timeline was estimated at approximately 6–7 years, with completion around 2032–2033.

- Progress is strongly dependent on substation upgrade schedules; delays in Substation 507 or 502 would directly impact the project.

- Test stand hardware procurement could begin in the near term, but facility design and construction are expected to lag due to limited engineering resources, particularly Andi’s availability.

4. Budget, Procurement, and Alternatives

- Preliminary cost estimates discussed:

  - SSAs: approximately $320K (R&K quote for 32 units)

  - Test facility construction: approximately $1.3M (prior F&O estimate)

- Xiaobiao emphasized interest in pursuing current-year procurement given favorable budget conditions. I has sent him estimated costs for facility upgrades, procurement, and labor requirements.

- Engineering support limitations were noted, with Andi currently unable to support detailed design work.

- An alternative location, Booster Building 140, was briefly discussed as a possible host for SSA equipment, contingent on clearing existing stored items.

- While SSA and test stand hardware procurement may be feasible in the short term, infrastructure and facility constraints limit near-term progress toward full deployment.

Action Items

- Javier

  - Follow up with F&O on substation details and timelines

  - Forward correspondence to Andi

  - Perform field walk-downs

  - Compile notes, sketches, and locate structural drawings

- Faya

  - Work with Jim to develop a high-level project timeline and the current proposal development schedule

- Rob

  - Develop rough SSA layout concepts (e.g., two-story configuration for 32 units)

  - Locate and share relevant construction drawings

- Andi

  - Coordinate with F&O

  - Provide input on utilities and code requirements when available