# Technical Note: 12.47KV Vacuum Contactor Controller
Electrical Connection Wiring Diagram

Source Document: id3088010601.pdf
Document Type: Technical Note – Circuit Schematic Analysis
Purpose: Detailed extraction of design information from circuit schematic for AI-assisted design reconstruction

────────────────────────────────────────────────────────────

# 1. Document Identification

## 1.1 Title Block Information

Title: 12.47K VAC CNTOR CONTROLLER – ELECTRICAL CONNECTION WIRING DIAGRAM

Drawing Number: ID-308-801-06-C1 (CAD version)

Original Drawing: ID-308-801-06 R0 (manual drawing, superseded)

Organization: Stanford Linear Accelerator Center (SLAC)

Affiliated: U.S. Department of Energy / Stanford University, Stanford, California

Project: Positron Electron Project 2 (PEP-II)

Scale: None (do not scale drawing)

SLAC Release: V:\MDCAD\DocumentControl\Images\Incoming\SLAC\PEP2 VCC1.dgn.tif

Release date: 9/25/2006 12:04:54 PM

## 1.2 Revision History

Original: Manual drawing ID-308-801-06 R0

C1: Redrawn to CAD and resized drawing from 'D' to 'E' size, revised per as-built, CoDCS

Date: 09/25 (September 2006)

## 1.3 Reference Drawings

GP-439-704-02: PEP2, ELECT SYSTEMS, 12.47KV OUTDOOR SWGR & VAC CNTOR, SCHEMATIC DIAGRAM

Ross Engineering DWG #713203: Vacuum contactor/driver schematic

# 2. Drawing Overview

This is the physical connection wiring diagram for the 12.47 kV vacuum contactor controller system. Unlike the schematic diagram (GP-439-704-02) which shows circuit logic, this drawing shows the actual physical wiring connections between equipment sections. It depicts the switchgear cabinet layout including the rear compartment, front view, swinging panel, and all inter-equipment wiring. The drawing documents how components are physically interconnected using terminal blocks, wire numbers, and cable routing between the switchgear, vacuum contactor driver, and external equipment.

# 3. Physical Layout Sections

## 3.1 Rear Compartment

12.47KV incoming line connections (OA, OB, OC phases)

#4-15KV cable connections

120VAC source connection

Incoming line enters from rear compartment

## 3.2 Front View

Contains main switchgear control panel

Current transformer connections

Protection relay panel

Terminal blocks TB3, TB4

Wire name column for identification

## 3.3 Swinging Panel (Rear View)

Houses switchgear door interlocks

Door interlocks shown in door 'CLOSED' position

Mounted on MTD (mounted on swinging panel) - SPEAR ONLY designation

Contains vacuum contactor driver (see Ross Engineering DWG #713203)

Panel reference: SD-1

# 4. Main Power Connections

## 4.1 Incoming 12.47KV Line

Phases: OA, OB, OC

Cable: #4-15KV rated

Feed from 120VAC source for control circuits

600A, 13.8KV switch rating

## 4.2 Load Side Connections

Surge arrestors: Connected to each phase on load side

Fuses: Protection on load side

Output to RF power supply transformer

## 4.3 Current Transformers

CT ratio: 50/5

CTs on each phase: X1, X2 secondaries

X1a, X1b, X1c - Phase CT primaries

X2a-P, X2e-P, X2-P - Phase CT secondaries with polarity markings

CT secondary connections routed to protection relays via terminal blocks

Current test block provided for maintenance testing

# 5. Terminal Block Wiring Details

## 5.1 TB3 - Main Switchgear Terminal Block

TB3 serves as the main interconnection point in the switchgear

Wire name column identifies each conductor

Numbered terminals: 1 through 22+

Connections to all relay panels, CTs, and external equipment

## 5.2 TB4 - Power/Auxiliary Terminal Block

TB4 terminals: Numbered 1-20+

TB4 carries CT secondary wiring

Connections to protection relay panel

MC contacts (MC3, MC4, MC5, MC7) for lockout relay and motor circuits

## 5.3 TB2 - Vacuum Contactor Terminal Block

TB2 terminals on vacuum contactor unit

Inter-wiring between TB2 and TB3

Wire name identification for each conductor

## 5.4 TBD - External/RFPS Terminal Block

TBD-1 through TBD-9: External connections to RF power supply

TBD-7: Oil pressure relief / overtemp monitoring

TBD-8: 86-L (BR) lockout relay external connection

TBD-9: RF power supply transformer connection

Connections to Ross Engineering DWG #713203

# 6. Protection and Control Panel Wiring

## 6.1 Relay Panel Connections

27 - Undervoltage relay

TX - Tripping relay

CR1 - Control relay 1

N - Neutral connection

OC, OB, OA - Phase designations

EE (RR) - Remote reset relay connections

CC - Control circuit identifiers

BB2 - Bus bar/terminal connections

## 6.2 Door Interlock Circuit

Switchgear door interlocks shown in 'CLOSED' position

SD-1 designation for door interlock switches

Multiple interlock contacts in series for safety

Wired to control circuit via dedicated terminals

## 6.3 Control Switches and Indicators

TRIP/RESET switch: Two-position control

86L - Lockout relay contact

NOT READY / READY indicators

OPEN / CLOSE position indicators

K3 relay connections for current sensing

# 7. Vacuum Contactor Section

## 7.1 Contactor Wiring

Vacuum contactor phases: C00, C31, C21, C11 (DC designations)

Phase capacitors: C32, C22, C12

Motor contacts: MC7, MC5, MC3, MC1 on each phase

4 sets of vacuum contactor poles shown (phases + spare)

Each pole: Terminals 1-10 with MC connections

## 7.2 Driver Section (Front View on Swinging Panel)

Driver for vacuum contactor: See Ross Engineering DWG #713203

Mounted on swinging panel (SPEAR ONLY)

Pressure switch connections

Temperature sensor connections

86L contact connections (BB1, BB2)

125V DC power connection

MC3, MC4 motor contactor connections

Terminal block for external connections

## 7.3 Lockout Relay and Motor Contactors

MC3: Motor contactor 3 - connected via TB3-10

MC4: Motor contactor 4

MC5: Motor contactor 5 - lockout relay

MC7: Motor contactor 7 - lockout relay

TB3-10, TB3-12 connections to lockout relay

AMG (6 connections) on term block box

# 8. Wire Numbering and Routing

## 8.1 Wire Name System

Wire names assigned in dedicated column on drawing

Numbered wire system (1-22+) for main control wiring

Alpha designations: CC, BB, EE, RR, SS for circuit functions

Cross-reference between terminal blocks using wire numbers

## 8.2 Major Wire Runs

TB3 to TB4: CT secondary and power connections

TB3 to TB2: Control wiring to vacuum contactor

TB3 to TBD: External connections to RFPS

Swinging panel to fixed panel: Door interlock wiring

CTs to relay panel: Current measurement wiring

# 9. Special Features

## 9.1 Space Heater

Space heater installed in switchgear enclosure

Connected via K4 relay

Prevents condensation in outdoor enclosure

## 9.2 Cabinet Temperature Sensor

Note: 'TO BE ADDED LATER' designation

Planned sensor for monitoring cabinet temperature

Connection points pre-wired

## 9.3 Oil Pump Transformer

Oil pump transformer connected in circuit

Associated with RFPS cooling system

Connected through TBD terminal block

# 10. Notes from Drawing

This drawing supersedes manual drawing ID-308-801-06 R0

Reference: GP-439-704-02 PEP2, ELECT SYSTEMS, 12.47KV OUTDOOR SWGR & VAC CNTOR, SCHEMATIC DIAGRAM

Driver for vacuum contactor: See Ross Engineering Co. DWG #713203

Swinging panel designation: MTD ON SWINGING PANEL (SPEAR ONLY)

Cabinet temperature sensor noted as 'TO BE ADDED LATER'

# 11. Operating Principles Summary

This connection wiring diagram documents the physical implementation of the 12.47 kV vacuum contactor controller system for SLAC's PEP-II accelerator. The drawing translates the circuit logic shown in the schematic diagram (GP-439-704-02) into actual wiring connections between three main equipment sections: the switchgear cabinet (with TB3 and TB4 terminal blocks), the vacuum contactor and its driver unit (with TB2 terminal block, mounted on a swinging panel), and the external RF power supply transformer (with TBD terminal block). The incoming 12.47 kV three-phase power enters through the rear compartment via #4-15KV cable, passes through current transformers (50/5 ratio) for protection relay measurement, and is switched by the vacuum contactor to the load. Protection is implemented through overcurrent relays (50-51) connected via a current test block, undervoltage relay (27), and a lockout relay system using motor contactors MC3/MC4/MC5/MC7. The vacuum contactor driver (Ross Engineering design) is mounted on a swinging panel for maintenance access and includes pressure switches, temperature monitoring, and 125VDC control power. Door interlocks ensure safe access to all compartments, with the energy storage capacitors automatically discharging when doors are opened. The 600A, 13.8KV rated switch provides the main disconnection capability for the system.