# Enerpro Modifications for SLAC HVPS

# Introduction

The SLAC accelerator SPEAR3 has a twelve-pulse, thyristor controlled, high voltage power supply (HVPS).  We are in the process of an upgrade of our HVPS controller, leaving the high-power part of the HVPS as is.  As part of this upgrade, we want to ensure that we use a modern circuit to generate the thyristor triggers for the supply and that we properly interface the rest of our controller to the trigger circuit.  This note documents our current controller and asks Enerpro for some detailed information and advice so that we can properly interface our controller with the Enerpro firing circuit.

# Existing System

The diagram of the power section of our HVPS is shown in Figure 1.

Figure 1:  HVPS schematic diagram.

The HVPS is capable of producing an output voltage of 90 kV and an output current of 27 A, for a total power of 2.5 MW.  It uses a twelve-pulse rectifier architecture.  Its input is a 12.47 kVAC, 3ϕ line, which feeds an extended delta, phase-shifting transformer.  This transformer feeds the primaries of two rectifier transformers.  The phase-shifting transformer advances the phase of one of these transformers by 15° and retards the phase of the other, also by 15°, with respect to the phase of the input line.  The centers of the primaries of each of these transformers are star connected to a six-pulse thyristor bridge that feeds a filter inductor.  Each of these transformers has two secondaries.  Each of the four secondary windings feeds a diode rectifier bridge.  The four bridges are connected in series to generate the final output.

The phase information about the input side of the HVPS is generated by monitor windings on the legs of the phase-shifting transformer.  As described above, these phases are not those of either of the primaries of the rectifier transformers; they lead the phases of one by 15° and lag the phases of the other by 15°.

Our current HVPS controller uses an Enerpro FCOG6100 Rev. K 3ϕ Firing Circuit with an FCOAUX60 Rev D Firing Board to initiate the thyristor triggers.  (Enerpro drawing number E128?)  The serial numbers of three of our boards are 41506, 50470, and 30045 for the FCOG6100 and 03198, 03813, and 1694 for the FCOAUX60.  The timing of the thyristor triggers is derived from the monitor windings on the legs of the phase-shifting transformer.  These are fed in as off-board phase references through R37, R38, and R39, each of which is 200 kΩ.  As seen in Figures 2 and 3, the amplitude of these signals is about 190 VPk-Pk on both HVPS1 and HVPS2.  Channel 1 on the scope trace is pin 5 of J5, the input of R39.  Channel 2 is pin 3 of J5, R38, and channel 3 is pin 1 of J5, R37.  Figure 2 also displays the oscilloscope-calculated phase to phase voltage between phases A and B.

Figure 2:  HVPS1 phase-shifting transformer monitor windings.

Figure 3:HVPS2 phase-shifting transformer monitor windings.

Figure 4:  Error signal from external controller.

We feed the SIGHI input of the Enerpro board from an external controller, which we will also redesign and rebuild during our upgrade project.  This controller consists of two parts, a programmed logic controller (PLC) and an analog regulator board.  A slow external software control system determines the target voltage of the HVPS, which it sends to the PLC.  From the target voltage, the PLC generates two analog output values.  One is an approximate value it calculates for SIGHI.  The second is the analog signal that it scales to be the reference for the analog regulator.  The analog regulator compares the readback of the HVPS with the reference and generates an error signal, which is weighted and added to the PLC analog output.  The SIGHI input to the Enerpro is the sum of these two signals.  Figure 4 shows a filtered version of the error signal.  Power line harmonics are clearly visible on the error signal.

# Proposed System Upgrade

Our proposed system upgrade for the controls will involve the purchase of new, current, Enerpro FCOG1200 12 Pulse Firing Board, Rev L(?), with perhaps some minor modifications to conform to our setup.  We will keep some parts of our existing controller but will replace the PLC and redesign our analog regulator.  We use this note as a means to better understand the FCOG1200, and to see which of our desired modifications are easy for Enerpro to make.

## Phase References

As described above, we have three external phase references that are related to, but offset by ±15° from, the phases of the primaries of the rectifier transformers.  As shown in figures 2 and 3, the peak-to-peak amplitude of these AC waveforms is ≈190 V.  We intend to input these waveforms to the Enerpro on connector J7.  Saul Rivera and David Prince, in a private communication, said that Enerpro can replace the resistor array RN4 (and possibly RN5, if required) with a header with two sets of three resistors so that, using the matched 0.033 μF capacitors C17 – C22, three of the phases into EP1016 will be advanced by 15° and three will be retarded by 15°.

Our existing monitor windings have a 500 Ω source impedance at the HVPS and then feed a 200 kΩ resistor at the input of the FCOG6100.  The FCOG6100 boards provide connector J5 and resistors R37 – R39 for use by external references.  On the FCOG1200 I see J7, but no place for the input resistors.  Does Enerpro recommend that we build a small adapter that will allow us to place these resistors?

The phase references then connect through 15 kΩ resistors in RN1 to +5 VDC.  The Thevenin equivalent circuit seen by RN2 is therefore a voltage of

VTH=15200.5+15⋅95 sin(2π⋅60⋅t)+200.5200.5+15⋅5=6.6125⋅sin2π⋅60⋅t+4.652

and a resistance of RTH=200.5⋅15200.5+15=13.956 kΩ.  The 6.6125 amplitude of the input sine wave added to the +5 VDC bias causes the voltage at the inputs of RN1 to go negative.  However, since the sum of the three phases always adds to 0 V, this should not pull down the +5 VDC reference voltage.  The inputs to the CMOS switch and the phase comparators are reduced from this value by the RC voltage dividers.

The input voltage seen at the phase reference comparators is then

VCOMPAC=-j2π⋅60⋅3.3×10-813.956+120×103-j2π⋅60⋅3.3×10-8VTHAC=-j80.381133.9-j80.381VTHAC

VCOMP=4.652+3.4034⋅sin2π⋅60⋅t∠-59.0°

What does Enerpro recommend for the desired sine wave amplitude at the input of the 15 kΩ resistors?

For our particular application we will need to bring in the external phase references on J7.  Since there are no places for input resistors between J7 and the phase detection circuitry, we will likely need to build a small board that will interface with our input signals and on which we can place the necessary resistors.  Your E640-FCOG1200 Rev L schematic lists J7 as a Part Number 640456-8, likely from TE.  Can you recommend a mating cable connector for J7?

On your legacy board, FCOG6100, E128 Rev I, I see that the outputs of the voltage dividers go to LM324 operational amplifiers, used as high gain comparators in your phase detection circuitry.  From my interpretation of the circuit, as long as the DC offset of the three signals is the same, the LM324 switching time is determined solely by the AC signal from the phases.  The schematic of the FCOG1200 does not give this detail; it places all of this circuitry inside of the Enerpro EP1016 integrated circuit.  Do the RC voltage dividers on the FCOG1200 also feed high gain analog comparators?  How is the bias level set for these comparators?

If I follow the idea discussed with Saul and David, build an adapter board to connect to J7 using the same 200 kΩ resistors between our input phase monitors, but have Enerpro modify the resistors RN4A – RN4C from 120 kΩ to 66.4 kΩ, I get
VCOMP=4.652+4.6758⋅sin2π⋅60⋅t∠-45.0°

If Enerpro changes RN4D – RN4F from 120 kΩ to 287 kΩ I get

VCOMP=4.652+1.7063⋅sin2π⋅60⋅t∠-75.0°

This resistor values seem to meet the desired phase shifts.  Are these values of the AC amplitudes acceptable?  This configuration of the adapter board would have our three phase inputs on one side, three 200 kΩ resistors on the board, and the outputs of Phase A connect to pins 1 and 4 of J7, Phase B to pins 2 and 5 of J7, and Phase C to pins 3 and 6 of J7.

Since we have to make an adapter board in any case, we could also make one with six resistors instead of three.  In that case we would make two sets of resistors for each phase.  The 200 kΩ resistors would feed pins 4 – 6 of J7 to create the 75° phase lag through the 287 kΩ resistors in RN4D – RN4F.  We would decrease the amplitude of the 45° phase lag by feeding pins 1 – 3 of J7 with 576 kΩ resistors and have Enerpro replace RN4A – RN4C with 66.5 kΩ resistors.  This would give a voltage at the comparator inputs of

VCOMP=4.8732+1.6957⋅sin2π⋅60⋅t∠-45.3°

The potential advantage of this approach is that the amplitudes are equal.  (Of course, by changing the resistors on our adapter board we could also change these amplitudes to another amplitude that you may prefer.)  The potential disadvantage is that now the DC offsets of the two phase triplets differ.  If your circuitry in EP1016 deals with each triplet separately this should not be a problem as all phases in each triplet will have the same offset.  If the EP1016 creates one common offset for all of the six signals together, then this may introduce timing errors between the triplets.

## Auto Balance Circuit

Since we do not have ability to independently monitor the outputs of our two secondary bridges, we will use neither the On-Board Auto-Balance Control nor the External Auto-Balance Control features.  Rather we will use the On-Board Trimpot Adjustment.  We will attempt to minimize the imbalance at our typical operating output voltage with an external error amplifier signal, shown in Figure 4, that will contribute to the SIGHI signal we will provide (see below).

## Input Bandwidth of the FCOG1200

As seen in Figure 4, the error signal that we observe in our analog regulator contains power line harmonics.  Because of the auto balance feature that is available in the FCOG1200, the inner timing loop of the circuit has sufficient bandwidth, “FCOG1200 Revision F Auto-Balance Circuit Amplifying Instructions” quotes a bandwidth >360 Hz, to act on the lower power line harmonics.  The standard input circuit of SIGHI is filtered by an RC filter with a time constant of τ=47.5×103⋅22×10-6=1.045 s, corresponding to a cutoff frequency of fC=1/2πτ=0.152 Hz.  Note 9 in the schematic says that this capacitor is optional.  Also, there was no such filter on the input of the FCOG6100.  Is there any problem with omitting C31 from the build of our boards?  What bandwidth can we expect from the FCOG1200?

## Voltage Controlled Oscillator Gain

Is the gain of the voltage-controlled oscillator that is controlled by the output of the PLL Summing Amplifier, U8B, still approximately 60⋅6⋅64/5 Hz/V=4608 Hz/V?  We are interested in this value so that we can model the dynamic system response.

## Interface to SIGHI

### Internal FCOG1200 Bias

As stated above, we will produce the SIGHI input to the FCOG1200 by adding a dynamic error signal from an analog feedback system to a static DC signal from a PLC DAC.  The legacy system uses the same configuration to drive the SIGHI input to the FCOG6100.  In the legacy system, SIGHI is terminated through R49 into the inverting input of U6, held at +5 VDC.  The SIGHI input to the FCOG1200 terminates into a high impedance input of a buffer amplifier that does not exist on the FCOG6100.  I would like to confirm this change between the two generations of Enerpro products so that we can properly modify the voltage we will send to the FCOG1200 in the SIGHI input.

### Safe Analog SIGHI Limits

Our PLC DAC will be unipolar.  Our regulator board error amplifier will be bipolar.  The output signal will come from a standard operational amplifier, so the maximum output current that can be sourced is in the 10-20 mA range fed into R26.  We want to avoid generating any voltage levels on SIGHI that will either damage the FCOG1200 or cause it to fail to operate properly.  If we order the FCOG1200 with its nominal SIGHI input voltage range of 0.8-5.8 V, at what maximum and minimum voltage levels on our regulator board should we clamp our output to SIGHI?