Introduction:  For this discussion we will be following the relevant parts of the PLC program that develop the reference signals that originate in the EPICS control system and then are delivered to the regulator board from the PLC via a scanner input module and an analog output module.  The two integers that we will be focusing on will be N7:10 & N7:11.  The chronological order of this will be a little off as the program is not really structured that way and I am going to go top to bottom and refer to everything by rung number.

RUNG 10 & 11: These are the first rung that these two integers are involved with and I would like to first explain the elements in these two rungs so things will be easier to read as we go.

B3:0/4, B3:0/2, B3:0/13 -  These are individual bits grouped in 16 bit words, B3 is the name of the array of 16 bit words, 0 is the number of the element (16 bit word) of that array and 4 is the bit in that word you are indexing.  In RSLogix 500 all bits must begin with B.  In this program Cassel also made a B9 bit array but it only had one element and searching did not turn up any instances of its use in the program.

XIC, XIO, OTE, OTL, OTU – These are bit functions, in rung 10 B3:0/4 is an XIC and B3:0/13 is OTL, and B3:0/2 is an OTE.  In rung 11 B3:0/2 is an XIO, and B3:0/13 is an OUT.  XIC is examine if closed, basically it is asking is this bit HIGH.  XIO is the opposite, it is asking is this bit low. OTE is output energize and this will make a bit go high for as long as what is in front of it is true.  OTL is output latch and will make a bit stay high until it is unlatched which is what the OTU is and stands for output unlatch.

N7:10, N7:11 - These are 16 bit integers, all integers in RSLogix 500 must start with N.  In this case N7 is the default array and these are the tenth and eleventh elements in this array.

MOV - This a built in function and it is as it seems.  The value of the source, in this case a constant 0, will be copied into the integer in the Destination.

TON, T4:5 DN, T4:14 DN - These are timer functions and bits.  T4 is the default array for timers. T4:5 is a TON timer and this means that when the rung goes true T4:5 will begin to time and will do so until the Accum = Preset in this case .01 * 300 = 3 seconds. Each timer has three useful bits the EN, TT, DN.  The TT and the DN are the most useful the TT stays high while the timer is timing and the DN bit goes high when the timer is done.  T4:14 DN is the done bit for a TOF timer that is used in a rung elsewhere in the program.  TON timers create time delays after a rung goes true, TOF timers create time delays after a rung goes false.

Rung 10 execution - Rung 10 starts with an XIC (examine if closed) bit operation.  The easy way to think of this is that this is asking the question is this bit HIGH, if so execute the rung, if not go to the next rung.  So let’s say it goes high, we then trigger the timer T4:5, and we latch the FAST INHIBIT Bit B3:0/13, three seconds later T4:5 will time out and the T4:5 DN will go high and so will B3:02 and stay that way until B3:0/4 changes state which would reset the timer.

Rung 11 execution - So as you may have figured out these two rungs are never true at the same time as rung 11 is true when B3:0/2 goes low.  When this rung is true whatever values that were in N7:10 and N7:11 will be replaced with 0.  T4:14 is a TOF timer in rung 36 that can be energized when any of four things happen, if any of those things goes LOW for more than three seconds then T4:14 DN would go HIGH and if rung 11 is true then B3:0/13 would be unlatched.

Rung 92 - The next relevant rung is rung 92, rung 92 only has N7:10 and uses some functions that have not been explained yet.

S:4/3 - This is a processor bit register that is included in every program and this register provides timing bits that have specific time periods and change states at a 50 % duty cycle. S:4/3 has a period of 160ms so this means it is high for 80ms and low for 80ms.

B3:5/8 - This is a normal bit but it is being used as an OSR( one shot rising) which is as it sounds.  This bit will toggle high on a positive transition of S:4/3 only one time(meaning only 1 scan) and then it will go low regardless of the status of S:4/3. A bit that is used as an OSR cannot be used elsewhere for other purposes.  Generally we would group and name OSR bits in a word or array so as to prevent using them elsewhere by mistake.

O:1.1-O1.5 – In slot 1 we have 1747-DCM(direct communication module)  this module is in a communication loop it is able to receive eight 16 bit words of information and send out eight 16 bit words of information.  O:1.1-O:1.7 are the location of the eight output words that are sent from the PLC to controls.

I:1.2 - This is the third 16 bit word of the input array of the 1747-DCM. So this is a number coming to the PLC from controls.

COP - This is a function very similar to the MOV function but where the MOV function is primarily designed to move one integer the COP function is designed more to move larger blocks of data. We are using integers here so the length of 8 in this case means that the 16 bit words from I:3.0-I:3.7 will be copied to the integers N7:100-N7:107.

GRT - This is fairly straight forward conditional statement. If A is greater than B  the function is true and whatever lies to the right of it will be executed.

Rung 92 execution - This rung is controlled by a combination of S:4/3 and B3:5/8.  S:4/3 will go high every 80ms, this will activate B3:5/8 and executer the rung one time during that scan.  The rungs on the right then should execute theoretically at the same time so I will list them top to bottom.

MOV - This is the first MOV function and this is taking the value of the AC current signal from the regulator board that is displayed on the touch panel N7:4 and sending to the control system via the second of the eight output words in the 1747- DCM.

COP - This is copying the input register from the thermocouple module in slot 3 I:3.0-I:3.7 to the integer memory locations N7:100-N7:107.

MOV - This is the same as the first move, here we are sending the value of the regulator voltage that we send to the regulator board to the control system via the third output word in the 1747-DCM.

MOV - This time we are moving the value of the high voltage monitor divider stored in N7:15 to the fourth output word in the 1747-DCM.

MOV - This time we are moving the DC Current value from the Danfysik current transformer to the fifth output word in the 1747-DCM.

MOV - This time we are moving a constant called maximum volts that is input from the touch panel to the sixth output word in the 1747-DCM.  Just for reference our 16 bit word has a sign bit for the fifteenth bit so the maximum number is 2^15 or 32,768. So this value would clamp the maximum volt just below the maximum number this integer could hold.

GRT and MOV - So I understand what this rung does but not why it does it but I think it will become clear once I have worked through the whole story of N7:10 so will likely update this more later.  Basically if N7:32(our Max Volt reference) is greater than N7:33 we send N7:33 to the sixth output of the 1747-DCM instead of N7:32.

MOV – Lastly we are simply taking the value of the third Input word of the 1747-DCM and moving it into N7:33.  This rung I think also will need some updating of details after I understand the whole story.