## binary inputs
PLC Code Tag | Identifier | Function | Indicator (Normal Op)
I:2/0 | 1-B3:12/0 | 120 VAC Control Power | On
I:2/1 | 1-B3:12/1 | A Phase Reference Voltage | On
I:2/2 | 1-B3:12/2 | Filter Inductor 1 | Off
I:2/3 | 1-B3:12/3 | Filter Inductor 2 | Off
I:6/0 | 1-B3:13/0 | SCR Disable Fiber Drive | Off
I:6/1 | 1-B3:13/1 | Crowbar Enable | Off
I:6/2 | 1-B3:13/2 | Crowbar Monitor | On
I:6/3 | 1-B3:13/3 | Klystron Arc Monitor | On
I:6/4 | 1-B3:13/4 | SCR Trigger 1 | Off
I:6/5 | 1-B3:13/5 | Transformer Arc Monitor | On
I:6/6 | 1-B3:13/6 | SCR Trigger 2 | Off
I:6/7 | 1-B3:13/7 | RF Crowbar | On
I:6/8 | 1-B3:13/8 | Ground Tank Oil Level | On
I:6/9 | 1-B3:13/9 | Ground Tank Switch | On
I:6/10 | 1-B3:13/10 | Crowbar Oil Level | On
I:6/11 | 1-B3:13/11 | SCR Oil Level | On
I:6/12 | 1-B3:13/12 | Key/Emergency Off Switch | On
I:6/13 | 1-B3:13/13 | Emergency Off | On
I:6/14 | 1-B3:13/14 | PPS 1 | On
I:6/15 | 1-B3:13/15 | PPS 2 | On
I:7/0 |  | Contactor Blocking Relay | Off
I:7/1 |  | Contactor Overcurrent Relay | Off
I:7/2 |  | Contactor Closed | On
I:7/3 |  | Contactor Ready | Off
I:7/4 |  | Transformer Pressure | On
I:7/5 |  | Transformer Vacuum | On
I:7/6 |  | Transformer Over Temperature | On
I:7/7 |  | Transformer Oil Level | On
I:7/8 |  | Transformer Sudden Pressure | On
I:7/9 |  | Oil Pump On | Off
I:7/10 |  | Spare | On
I:7/11 |  | Enerpro Phase Loss | On
I:7/12 |  | Regulator Current Limit | Off
I:7/13 |  | Ground Tank Relay | On
I:7/14 |  | Regulator Voltage Trip | Off
I:7/15 |  | Regulator Current Trip | Off

## binary outputs
PLC Code Tag | Identifier | Function | Indicator (Normal Op)
O:2/0 |  | AC Bias Power Supply | On
O:2/1 |  | 120 VDC Power Supply | On
O:2/2 |  | 240 VDC Power Supply | On
O:2/3 |  | Ground Tank Relay Coil | On
O:5/0 |  | SCR Enable | On
O:5/1 |  | Contactor On | On
O:5/2 |  | Contactor Enable | On
O:5/3 |  | Force Crowbar | Off
O:5/4 |  | Crowbar Off | On
O:5/5 |  | Enerpro Slow Start | Off
O:5/6 |  | Enerpro Fast Inhibit | On
O:5/7 |  | Regulator Reset | Off

## binary bits summary
Register
Bit | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
B3:0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1
B3:1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B3:2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
B3:3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B3:4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## B3_0
Register B3:0
Bit No. | Hex | Label | Rungs Set
15 | 8000 | Contactor Ready | 30
14 | 4000 | Alarm Reset | 1,7, 14, 20, 21, 22, 23, 24, 25, 26, 28, 29, 37
13 | 2000 | Fast Inhibit | 10, 13
12 | 1000
11 | 800
10 | 400 | Reset | 1
9 | 200 | No Xformer Fault | 61
8 | 100 | Contactor Latch | 2
7 | 80
6 | 40 | Enable | 17
5 | 20
4 | 10 | SCR On Latch | 4
3 | 8
2 | 4 | Regulator On | 10
1 | 2
0 | 1 | Off Display | 16

## B3_1
Register B3:1
Bit No. | Hex | Label | Rungs Set
15 | 8000 | Supply On | 74
14 | 4000 | SCR On | 74
13 | 2000 | System Ready | 3
12 | 1000 | 12kV On | 38
11 | 800 | Contactor Closed Disp | 33
10 | 400 | Contactor Ctrl Pwr Display | 40
9 | 200 | Enable Display | 17
8 | 100 | Aux Pwr On Display | 63
7 | 80 | Crowbar On | 37
6 | 40 | SCR Off | 75
5 | 20 | System Not Ready | 34
4 | 10 | 12kV Off | 39
3 | 8 | Contactor Open Disp | 31
2 | 4 | Disable Display | 64
1 | 2 | PPS On | 15
0 | 1 | Emergency Off | 14

## B3_2
Register B3:2
Bit No. | Hex | Label | Rungs Set
15 | 8000
14 | 4000
13 | 2000
12 | 1000
11 | 800
10 | 400
9 | 200
8 | 100
7 | 80 | Water Flow Switch | 50
6 | 40 | Klystron Crowbar Latch | 48
5 | 20 | Klystron SCR Bit | 49
4 | 10 | Klystron Crowbar | 56
3 | 8 | Phase Loss | 51
2 | 4 | Contactor OK | 58
1 | 2 | Xformer Latched OK | 60
0 | 1 | Ground Switch Open | 73

## B3_3
Register B3:3
Bit No. | Hex | Label | Rungs Set
15 | 8000 | SCR Driver Up Latch | 26
14 | 4000
13 | 2000 | SCR Driver Latch | 25
12 | 1000 | Contactor Over Current Alarm | 24
11 | 800 | Emergency Off Alarm | 14
10 | 400 | Aux Power Alarm | 28
9 | 200 | Regulator Trip | 29
8 | 100 | Contactor Alarm | 20
7 | 80 | Xformer Alarm | 21
6 | 40 | Regulator Over Voltage | 23
5 | 20 | Regulator Over Current | 22
4 | 10
3 | 8
2 | 4 | Open Load Latch | 7
1 | 2 | Crowbar | 37
0 | 1 | Alarm | 19

## B3_4
Register B3:4
Bit No. | Hex | Label | Rungs Set
15 | 8000 | Xformer Arc Trip | 57
14 | 4000 | Ground Tank Oil Level | 52
13 | 2000 | Klystron Arc Trip | 55
12 | 1000 | Over Voltage Latch | 54
11 | 800 | Over Current Latch | 53
10 | 400 | Crowbar Latch | 13
9 | 200 | SCR 2 Latch | 72
8 | 100 | SCR 1 Latch | 71
7 | 80 | Oil Pump Flow | 47
6 | 40 | DC Power Fault | 59
5 | 20 | Over Current Trip Latch | 58
4 | 10 | Sudden Pressure | 46
3 | 8 | Low Oil | 45
2 | 4 | SCR Oil Tank Level | 44
1 | 2 | Oil Temp | 43
0 | 1 | Pressure Latch | 41

## B3_5
Register B3:5
Bit No. | Hex | Label | Rungs Set
15 | 8000
14 | 4000
13 | 2000
12 | 1000 | Vacuum Latch | 42
11 | 800 | SCR 2 Status | 71
10 | 400 | SCR 1 Status | 72
9 | 200
8 | 100
7 | 80
6 | 40
5 | 20
4 | 10
3 | 8 | Enerpro Phase Loss | 1, 116
2 | 4
1 | 2
0 | 1

## touch panel interlocks
PLC Code Tag | Identifier | Function All illuminated OK during normal op
| 1-B3:4/11 | AC Overcurrent Fault
| 1-B3:3/6 | DC Overvoltage OK
| 1-B3:3/5 | DC Overcurrent OK
| 1-B3:13/8 | Ground Tank Oil Fault
| 1-B3:1/0 | Ground Tank E-Stop OK
| 1-B3:1/7 | Crowbar OK
| 1-B3:4/13 | Klystron Arc Fault
| 1-B3:4/15 | Transformer Arc Fault
| 1-B3:2/4 | Klystron Crowbar Fault
| 1-B3:3/2 | Open Load OK
| 1-B3:3/14 | H1 SCR Drivers OK
| 1-B3:3/15 | H2 SCR Drivers OK
| 1-B3:13/11 | SCR Oil Level Low
| 1-B3:13/10 | Crowbar Oil Level Low
| 1-B3:14/7 | Main Tank Oil Level Low
| 1-B3:14/6 | Oil Temperature Fault
| 1-B3:2/7 | Oil Flow Switch Fault
| 1-B3:14/4 | Pressure Fault
| 1-B3:14/8 | Relief Valve Fault (Sudden Pressure?)
| 1-B3:14/5 | Vacuum Fault
| 1-B3:0/3 | Summary Not Ready
| 1-B3:5/12 | Vacuum Fault
| 1-B3:4/10 | Pressure Fault Latched
| 1-B3:4/1 | Oil Temperature Fault Latched
| 1-B3:4/2 | SCR/Crowbar Oil Level Low Latched
| 1-B3:4/3 | Main Tank Oil Level Low Latched
| 1-B3:4/4 | Sudden Pressure Fault Latched

## analog registers
PLC Code Tag | Identifier | Function | Value (500 mA, 2850 kV) | Rungs
N7:0 | 1-N7:0 | Requested DC Volts (kV) | 7080
N7:1 | 1-N7:1 | Phase Angle | 442
N7:2 | 1-N7:2 | Regulator Voltage | 7497 | 84, 85, 87
N7:3 | 1-N7:3 | Phase Angle Monitor | 354 | 88, 89
N7:4 | 1-N7:4 | AC Amps | 36, should be 1036. Format error on display? | 90, 91, 92, 93
N7:5 | 1-N7:5 | Volt Monitor 1 | 75, should be ~7500. Format error on display?
N7:6 | 1-N7:6 | Volt Monitor 2 | 7399
N7:7 | 1-N7:7 | DC Amps | 2187
N7:8 | 1-N7:8 | Power | 1783
N7:9 | 1-N7:9 | AC Amp Offset | -117 | 78
N7:10 | 1-N7:10 | Reference Out (EL1 input on regulator) | 23167 | 11, 92, 104, 105, 106, 108, 112
N7:11 | 1-N7:11 | Phase Out (PLC contribution to SIG HI) | 14488
N7:12 | 1-N7:12 | Feedback Voltage | 24375 | 76, 77, 84
N7:13 | 1-N7:13 | Phase Ang Monitor (SIG HI input on Enerpro) | 11585 | 88
N7:14 | 1-N7:14 | AC Current Monitor | 7374 | 08, 78, 79, 90, 93
N7:15 | 1-N7:15 | Voltage Monitor 1 | 24438 | 08, 80, 86, 92, 95, 98
N7:16 | 1-N7:16 | Voltage Monitor 2 | 24215 | 08, 81, 100
N7:17 | 1-N7:17 | DC Current Monitor | 14330 | 08, 82, 83, 92, 94, 95, 102
N7:18 | 1-N7:18 | Power Calculation | 10724 | 95, 96, 97, 114
N7:19 | 1-N7:19 | Offset Feedback | -122 | 76
N7:20 | 1-N7:20 | Output Reference Multiplier | 10000
N7:21 | 1-N7:21 | Phase Angle Multiplier | 1000
N7:22 | 1-N7:22 | Voltage Multiplier | 75, should be 10075. Format error on display? | 84
N7:23 | 1-N7:23 | Phase Angle Multiplier | 1000
N7:24 | 1-N7:24 | AC Current Multiplier | 4600
N7:25 | 1-N7:25 | Voltage Monitor 1 Multiplier | 10000
N7:26 | 1-N7:26 | Voltage Monitor 2 Multiplier | 10000
N7:27 | 1-N7:27 | DC Current Multiplier | 5000
N7:28 | 1-N7:28
N7:29 | 1-N7:29 | Power Multiplier | 6
N7:30 | 1-N7:30 | External Reference | 23134 | 104
N7:31 | 1-N7:31 | Internal Reference | 100 | 104, 105
N7:32 | 1-N7:32 | Max Internal Reference | 32000 | 92, 105
N7:33 | 1-N7:33 | Max External Reference | 26869 | 92, 104
N7:34 | 1-N7:34 | Plot Volts | 174
N7:35 | 1-N7:35 | Plot Current | 148
N7:36 | 1-N7:36 | Plot Power | 10075
N7:37 | 1-N7:37 | Display Volts | 76
N7:38 | 1-N7:38 | Display Current | 72
N7:39 | 1-N7:39 | Display Power | 66
N7:40 | 1-N7:40 | Phase Angle Multiplier | 12000
N7:41 | 1-N7:41 | Add Offset | 6000
N7:42 | 1-N7:42 | Max Phase Angle | 18000
N7:43 | 1-N7:43 | Delta | 0
N7:44 | 1-N7:44 | Div Plot Volts | 43
N7:45 | 1-N7:45 | Div Plot Current | 7
N7:46 | 1-N7:46 | Div Plot Power | 260
N7:47 | 1-N7:47 | Div Meter Volts | 320
N7:48 | 1-N7:48 | Div Meter Current | 198
N7:49 | 1-N7:49 | Div Meter Power | 162
N7:71 |  | Maximum voltage (loaded at startup?) | 32000 | 105
N7:72 |  | Maximum phase angle (loaded at startup?) | 18000 | 105
N7:73 |  | Internal reference (loaded at startup?) | 100 | 105
N7:74 |  | Maximum voltage divided by Reference out |  | 105
N7:75 |  | Internal reference divided by Reference out |  | 105
N7:110 | 1-N7:110 | Temp Sense Ch 0 (Phase Upper TC?) | 55
N7:111 | 1-N7:111 | Temp Sense Ch 1 (Phase Lower TC?) | 56
N7:112 | 1-N7:112 | Temp Sense Ch 2 (Crowbar Tank?) | 40
N7:113 | 1-N7:113 | Temp Sense Ch 3 (Control Cabinet?) | 32
Fuel Gauges
|  | Volts KV | 74.97
|  | Amps DC | 21.91
|  | Amps Line AC | 103.6

## analog inputs
Module | Slot | Number | Function
AB-1746-NIO4V | 8 | 0 | Output voltage monitor from regulator card (J3-1)
AB-1746-NIO4V | 8 | 1 | Readback of phase control voltage to Enerpro input (SIG HI)
AB-1746-NI4 | 9 | 0 | Input AC current monitor from regulator card (J3-2)
AB-1746-NI4 | 9 | 1 | Output voltage monitor 1 from HVPS (splits to J1-1 of reg)
AB-1746-NI4 | 9 | 2 | Output voltage monitor 2 from HVPS
AB-1746-NI4 | 9 | 3 | Output DC current monitor (Danfysik) from grounding tank

## analog outputs
Module | Slot | Number | Function
AB-1746-NIO4V | 8 | 0 | Reference voltage setpoint to regulator card input (EL1)
AB-1746-NIO4V | 8 | 1 | Contribution to SIG HI phase control input of Enerpro (1k res)

## inputs from VXI DCM
Bank | Register | Function
I:1 | 1 | External Reference from VXI DCM
I:1 | 2 | Maximum External Reference from VXI DCM

## outputs to VXI DCM
Bank | Register | Function
O:1 | 1 | AC Current to VXI DCM
O:1 | 2 | Reference Out Voltage to EL1 to VXI DCM
O:1 | 3 | HVPS Voltage Monitor 1 to VXI DCM
O:1 | 4 | HVPS Current Monitor (Danfysik) to VXI DCM
O:1 | 5 | Maximum Internal Voltage Reference to VXI DCM

## SPEAR RF Klystron HVPS EPICS
Label | Value | Device Type | Raw Value | HW Mask | ESLO | VAL | Decimal (may include extra 32768)
Contactor Closed | CLOSED | AB-16 bit BI | 0x20 | 0x20
Contactor Open | CLOSED | AB-16 bit BI | 0x0 | 0x80
Contactor Status | ON | AB-16 bit BI | 0x40 | 0x40
Contactor Ready | READY | AB-16 bit BI | 0x100 | 0x100
Klys Output Pwr | 747 | IQA Module 1 Calc
Klys Coll Pwr | 843 | Calc
Klys Efficiency | 46.94 | Calc
RF PLC Voltage | 72.4 | AB-1771DCM AI-13 bit raw | 0x1B0A |  | 0.02442 | 72.5 | 6922
RF PLC Current | 22.09 | AB-1771DCM AI-13 bit raw | 0x1711 |  | 0.01221 | 22.09 | 5905
RF PLC Coll Pwr | 973 | Calc
Klys Perveance | 1.13 | Calc
HVPS Current | 21.92 | AB-SLC500DCM-Signed | 0xB81E |  | 0.00153 | 21.92 | 47134
HVPS Voltage | 72.47 | AB-SLC500DCM-Signed | 0xDCD3 |  | 0.00305 | 72.52 | 56531
HVPS Power | 1589 | Calc
Max Volt Status | ACTIVE | AB-16 bit BI | 0x1 | 0x1
Regulator Voltage | 72.28 | AB-SLC500DCM-Signed | 0xDC83 |  | 0.00305 | 72.29 | 56451
Max Voltage Rbck | 82 | AB-SLC500DCM-Signed | 0xE8F5 |  | 0.00305 | 82 | 59637
Over Voltage | OK | AB-16 bit BI | 0x2 | 0x2
Klystron Arc | OK | AB-16 bit BI | 0x10 | 0x10
Transformer Arc | OK | AB-16 bit BI | 0x400 | 0x400
Crowbar | OK | AB-16 bit BI | 0x0 | 0x200
Crowbar from RF | OK | AB-16 bit BI | 0x800 | 0x800
Emergency Off | OK | AB-16 bit BI | 0x0 | 0x800
AC Current | OK | AB-16 bit BI | 0x8 | 0x8
Over Temperature | OK | AB-16 bit BI | 0x1 | 0x1
Oil Level | OK | AB-16 bit BI | 0x4000 | 0x4000
Transformer Press | OK | AB-16 bit BI | 0x40 | 0x40
Transfmr Vac/Press | OK | AB-16 bit BI | 0x80 | 0x80
Open Load | OK | AB-16 bit BI | 0x0 | 0x200
AC Current | 113.29 | AB-SLC500DCM-Signed | 0x9D09 |  | 0.01526 | 113.43 | 40201
12 kV Available | AVAIL | AB-16 bit BI | 0x2 | 0x2
AC Auxiliary Pwr | ON | AB-16 bit BI | 0x4 | 0x4
DC Auxiliary Pwr | ON | AB-16 bit BI | 0x400 | 0x400
Enerpro Fast Inhibit | ON | AB-16 bit BI | 0x1000 | 0x1000
Enerpro Slow Start | ACTIVE | AB-16 bit BI | 0x0 | 0x2000
Supply Status | ON | AB-16 bit BI | 0x10 | 0x10
Supply Ready | READY | AB-16 bit BI | 0x20 | 0x20
PPS | PERMIT | AB-16 bit BI | 0x0 | 0x100
SCR 1 | ON | AB-16 bit BI | 0x4 | 0x4
SCR 2 | ON | AB-16 bit BI | 0x8 | 0x8

## DCM-FULL bits
0002, 0006 | I1 | 48 | Remote On/Off
0004, 0009 | I:1 | 64 | Control Enable
115 | I:1 | 80 | Control reset
104 | O:1 | 96 | (overflow? x3)
38 | O:1 | 97 | 12kV on
62 | O:1 | 98 | AC aux power on
53 | O:1 | 99 | AC current trip
55 | O:1 | 100 | (klystron) Arc trip
32 | O:1 | 101 | Contactor closed
30 | O:1 | 102 | Contactor enable
31 | O:1 | 103 | Contactor open
40 | O:1 | 104 | Contactor ready
37 | O:1 | 105 | Crowbar on
63 | O:1 | 106 | Auxiliary power
14 | O:1 | 107 | Emergency off
12 | O:1 | 108 | Enerpro fast inhibit
35 | O:1 | 109 | Enerpro slow start
45 | O:1 | 110 | Low oil
43 | O:1 | 111 | Oil overtemp
43 | O:1 | 112 | Overtemp
54 | O:1 | 113 | Over volt latch
72 | O:1 | 114 | SCR 1 status
71 | O:1 | 115 | SCR 2 status
4 | O:1 | 116 | Supply Ready
3 | O:1 | 117 | System Ready
46 | O:1 | 118 | Sudden pressure
41 | O:1 | 119 | Pressure alarm
15 | O:1 | 120 | PPS status
7 | O:1 | 121 | Remote Open Load
57 | O:1 | 122 | (xfmr arc trip)
56 | O:1 | 123 | DCM bit (Signal from F.O. Crowbar Enable from LLRF)
25 | O:1 | 124 | H1 SCR latch
26 | O:1 | 125 | H2 SCR latch
42 | O:1 | 126 | Vacuum alarm