| Environment, Safety & Health Division | Chapter 8: Electrical Safety # Electrical Work Plan Form Product ID: 249 ¦ Revision ID: 2312 ¦ Date Published: 15 June 2021 ¦ Date Effective: 15 June 2021 URL: https://www-group.slac.stanford.edu/esh/eshmanual/references/electricalFormEWP.pdf ¦ docx |
| --- | --- |

All electrical work at SLAC requires the prior completion of an electrical work plan (EWP) or equivalent work planning and control (WPC) documentation. For certain energized work, an energized electrical work permit (EEWP) is also required. (See Chapter 8, “Electrical Safety”, Section 10.3.)

| Job / activity: Work within SPEAR HVPS Phase Tank |  | Start date: 9/11/2023 | Valid through: (1 year max) |
| --- | --- | --- | --- |
| Prepared by (print): Tony Beukers | Signature: |  | Date: |
| Person in charge (print): Marc Larrus | Signature: |  | Date: |
| Other reviewer (print): Jim Sebek | Signature: |  | Date: |
| Scope of work summary: Access and work within either SPEAR1 or SPEAR2 HVPS phase tank. |  |  |  |

# Hazard Analysis (add rows as needed)

| Step or Task | Step or Task Description | Hazard (include shock and arc flash hazard information from the hazard label affixed to the equipment or from the electrical analysis engineer) | Control (include electrical safety PPE based on the electrical hazard information) |
| --- | --- | --- | --- |
|  | Electrical: Isolate energy sources to both SPEAR HVPSs. | 12.47 kV 3ph, AC (shock and arc flash hazard) 200 V pulses to thyristor triggers, fed by locked out 120 VAC. | Perform “SPEAR3 RF HVPS Energy Isolation Plan” (SR-444-636-02-R1). This locks out energy sources and grounds the output for both SPEAR HVPSs. Note, if planning to perform maintenance on a supply while the other is turned-on, an additional procedure that describes the correct lockout condition and the removal/shorting of the output cable from the switch tank is required. |
|  | Mechanical: Remove oil from tank | ~100 gallons of vegetable derived oil is a spill hazard | If transferring oil outside of building 514 secondary containment then oil containers must be stored in another means of secondary containment. Workers must have received OJT and have ‘Spill Prevention and Response Training’ (course 169) on their STA. |
|  | Mechanical: Prepare work area | Trip/Slip | Upon entering the top of the supply, familiarize self with trip hazards and clean up oil and dirt. |
|  | Mechanical: Remove phase tank cover plate | ~70 lbs lift hazard. | Must have 2 people to remove cover |
|  | Electrical: Work within phase tank. | 12.47 kV, 0.03 uF (2 x 0.015 uF) snubber capacitors across each phase stack. | For both the high side AND low side SCR stacks: Use two dedicated Phenix soft ground sticks to short from the filter inductor to the three SCR transformer taps. When measuring the SCR snubber resistors, reinstall them afterwards to avoid dielectric recharging of the snubber capacitors. |
|  | Mechanical: Work in phase tank | Bumps, bruises, and strain | Must have physical ability to safely perform the work. Removal of SCR stacks is particularly difficult. Requires foam/rubber pads, maintenance blankets. Note: should rotate stacks long ways to drain captured oil from them over tank before moving them to side. |
|  | Mechanical: Transporting heavy or awkward parts to and from the top of the power supplies. | Strain and trip hazard carrying awkward/heavy items up and down the stairs from the top of the power supply. | The SSRL mechanical services group (MSG) has a lifting basket staged next to the HVPS. Bulky and/or awkward components that need to be transported to and from the top of the HVPS are lifted in the basket by a forklift operated by the MSG. Workers on the HVPS should coordinate the movement of these components with MSG. |

# Authorization

| Authorizer (administrative or functional supervisor, foreman, POC). I have reviewed the steps, hazards and controls described in this EWP. Workers are qualified (that is, licensed or certified, as appropriate, and in full compliance with SLAC training requirements) to perform this activity. |  |  |
| --- | --- | --- |
| Name (print): | Signature: | Date: |

# Release

| Area or building manager Red work? Yes. Document release via WIP and tailgate meeting. No. I have communicated unique area hazards, boundary conditions, and so on with the authorizer or listed worker(s) and have coordinated this job with affected occupants. Listed workers are released to perform described scope of work. |  |  |
| --- | --- | --- |
| List boundary conditions, notes, etc: |  |  |
| Name (print): | Signature: | Date: |

# Worker Acknowledgement (add rows as needed)

| Worker. I understand and will adhere to the steps, hazards, and controls in this EWP. I understand that performing steps out of sequence may pose hazards that have not been evaluated nor authorized. I will contact the person who authorized my work before continuing if the scope of work changes or new hazards are introduced. I understand my stop work authority and responsibility. |  |  |
| --- | --- | --- |
| Name (print) | Signature | Date |

# Electrical Work Procedure 
(optional: insert or attach procedure(s), LOTO energy isolation plan(s) and associated drawings/sketches below)

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]