| Environment, Safety & Health Division | Chapter 8: Electrical Safety # Electrical Work Plan Form Product ID: 249 ¦ Revision ID: 2312 ¦ Date Published: 15 June 2021 ¦ Date Effective: 15 June 2021 URL: https://www-group.slac.stanford.edu/esh/eshmanual/references/electricalFormEWP.pdf ¦ docx |
| --- | --- |

All electrical work at SLAC requires the prior completion of an electrical work plan (EWP) or equivalent work planning and control (WPC) documentation. For certain energized work, an energized electrical work permit (EEWP) is also required. (See Chapter 8, “Electrical Safety”, Section 10.3.)

| Job / activity: Work within SPEAR HVPS main tank |  | Start date: 9/11/2023 | Valid through: (1 year max) |
| --- | --- | --- | --- |
| Prepared by (print): Tony Beukers | Signature: |  | Date: |
| Person in charge (print): Marc Larrus | Signature: |  | Date: |
| Other reviewer (print): Jim Sebek | Signature: |  | Date: |
| Scope of work summary: Access and work within either SPEAR1 or SPEAR2 HVPS main tank. |  |  |  |

# Hazard Analysis (add rows as needed)

| Step or Task | Step or Task Description |  |  | Hazard (include shock and arc flash hazard information from the hazard label affixed to the equipment or from the electrical analysis engineer) |  | Control (include electrical safety PPE based on the electrical hazard information) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Electrical: Isolate energy sources to both SPEAR HVPSs. |  |  | 90 kV / 27 A, DC 12.47 kVAC mains 120 VAC for oil pump 125 VDC control power for main tank interlocks 8 kJ stored in capacitors, 90 kV |  | Perform “SPEAR3 RF HVPS Energy Isolation Plan” (SR-444-636-02-R1). This locks out energy sources and grounds the output for both SPEAR HVPSs. Note, if planning to perform maintenance on a supply while the other is turned-on, an additional procedure that describes the correct lockout condition and the removal/shorting of the output cable from the switch tank is required. |  |
|  |  | Mechanical: Prepare work area |  |  | Trip/Slip |  | Upon entering the top of the supply, familiarize self with trip hazards and clean up and oil and dirt. |
|  | Mechanical: Remove cables/conduits |  |  | Trips, prohibit lid removal |  | -Valve off and remove nitrogen line. -Disconnect cables and remove over-pressure/under-pressure conduit. -Disconnect cabling to rapid pressure release valve. |  |
|  |  | Electrical: Work within the main tank |  |  | 90 kV, 0.22 uF output cap 30 kV, 4 each: 8 uF filter caps 30 kV, 4 each: 0.24 uF crowbar SCR snubbers |  | Execute all electrical steps of the ‘Work with the SPEAR HVPS crowbar tank” EIP. This includes the three steps required to safe the filter caps and output cap and ground the output cap. |
|  | Electrical: Work within the main tank |  |  | 12.7 kV, 12 stacks with 0.30 uF snubbers (2 x .015 uF) |  | Execute all electrical steps of the ‘Work with the SPEAR HVPS phase tank” EIP. Alternatively, may be able to use two Phenix discharge sticks to soft and then hard short between at least one side of each filter inductor and a point on the primary magnetics. This would be done once access is made into the main tank. |  |
|  | Mechanical: Remove low and/or high side main tank cover | Cover could drop unexpectedly during move with chain hoist. Covers weigh ~300 lbs each. | Chain hoist must be used to move covers. The chain hoist safety inspection must be current. The operators must be trained in ES&H courses 280 and 280 PRA. The operators must have an approved ordinary lifting plan. Wear safety toes non-slip shoes. |
|  | Mechanical: Remove oil from tank |  |  | Removing 1200 gallons of vegetable derived oil is a spill hazard |  | If transferring oil outside of building 514 secondary containment then oil containers must be stored in another means of secondary containment. Workers must have received OJT and have ‘Spill Prevention and Response Training’ (course 169) on their STA. Removing more than 1200 gallons can expose the power supply magnetics to air, risking permanent damage of the HVPS. There are 2600 gallons of oil in the main tank. |  |
|  | Electrical: Work on oil pump or within 1 foot of AC terminal block | 120 VAC shock hazard. | ZVV incoming AC to pump at terminal block. |
|  | Mechanical: Transporting heavy or awkward parts to and from the top of the power supplies. |  |  | Strain and trip hazard carrying awkward/heavy items up and down the stairs from the top of the power supply. |  | - The SSRL mechanical services group (MSG) has a lifting basket staged next to the HVPS. Bulky and/or awkward components that need to be transported to and from the top of the HVPS are lifted in the basket by a forklift operated by the MSG. Workers on the HVPS should coordinate the movement of these components with MSG. |  |

# Authorization

| Authorizer (administrative or functional supervisor, foreman, POC). I have reviewed the steps, hazards and controls described in this EWP. Workers are qualified (that is, licensed or certified, as appropriate, and in full compliance with SLAC training requirements) to perform this activity. |  |  |
| --- | --- | --- |
| Name (print): | Signature: | Date: |

# Release

| Area or building manager Red work? Yes. Document release via WIP and tailgate meeting. No. I have communicated unique area hazards, boundary conditions, and so on with the authorizer or listed worker(s) and have coordinated this job with affected occupants. Listed workers are released to perform described scope of work. |  |  |
| --- | --- | --- |
| List boundary conditions, notes, etc: |  |  |
| Name (print): | Signature: | Date: |

# Worker Acknowledgement (add rows as needed)

| Worker. I understand and will adhere to the steps, hazards, and controls in this EWP. I understand that performing steps out of sequence may pose hazards that have not been evaluated nor authorized. I will contact the person who authorized my work before continuing if the scope of work changes or new hazards are introduced. I understand my stop work authority and responsibility. |  |  |
| --- | --- | --- |
| Name (print) | Signature | Date |

# Electrical Work Procedure 
(optional: insert or attach procedure(s), LOTO energy isolation plan(s) and associated drawings/sketches below)

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]