| Environment, Safety & Health Division | Chapter 8: Electrical Safety # Electrical Work Plan Form Product ID: 249 ¦ Revision ID: 2312 ¦ Date Published: 15 June 2021 ¦ Date Effective: 15 June 2021 URL: https://www-group.slac.stanford.edu/esh/eshmanual/references/electricalFormEWP.pdf ¦ docx |
| --- | --- |

All electrical work at SLAC requires the prior completion of an electrical work plan (EWP) or equivalent work planning and control (WPC) documentation. For certain energized work, an energized electrical work permit (EEWP) is also required. (See Chapter 8, “Electrical Safety”, Section 10.3.)

| Job / activity: Work within SPEAR HVPS crowbar tank |  | Start date: 01/05/2024 | Valid through: 01/01/2025 (1 year max) |
| --- | --- | --- | --- |
| Prepared by (print): Tony Beukers | Signature: |  | Date: |
| Person in charge (print): Marc Larrus | Signature: |  | Date: |
| Other reviewer (print): Jim Sebek | Signature: |  | Date: |
| Scope of work summary: Access and work within either SPEAR1 or SPEAR2 HVPS crowbar tank. |  |  |  |

# Hazard Analysis (add rows as needed)

| Step or Task | Step or Task Description | Hazard (include shock and arc flash hazard information from the hazard label affixed to the equipment or from the electrical analysis engineer) | Control (include electrical safety PPE based on the electrical hazard information) |
| --- | --- | --- | --- |
|  | Electrical: Isolate energy sources to both SPEAR HVPSs. | 90 kV / 27 A, DC 8 kJ stored in capacitors, 90 kV | Perform “SPEAR3 RF HVPS Energy Isolation Plan” (SR-444-636-02-R1). This locks out energy sources and grounds the output for both SPEAR HVPSs. Note, if planning to perform maintenance on a supply while the other is energized and operational, an additional procedure “SPEAR3 RF HVPS Switch Procedure with Work Done on Idle Supply” (SR-444-636-04-R1) must be executed. This procedure describes the correct lockout condition and the removal/shorting of the output cable of the supply to be worked on from the switch tank. |
|  | Mechanical: Remove oil from tank | 135 gallons of vegetable derived oil is a spill hazard | If temporarily transferring oil outside of building 514 secondary containment for storage, then the oil containers must be stored in another means of secondary containment, such as a portable berm. Workers must have received the necessary OJT. Required completed SLAC training on worker’s STA includes: 103: Hazard Communication; 105/R Hazardous Waste Management and 169: Spill Prevention and Response Training. |
|  | Mechanical: Prepare work area | Trip/Slip | Upon entering the top of the supply, familiarize yourself with trip hazards. Clean up any oil and dirt that could lead to falls. |
|  | Mechanical: Remove nitrogen supply line | Oxygen deficiency | -Valve off the nitrogen supply line on the wall of B514. -Remove the nitrogen supply line from main tank lid -Apply a clamshell with an administrative lock and tag to HVPS lid connection to which the nitrogen line is normally connected. The tag should indicate “Do Not Connect” |
|  | Mechanical: Remove crowbar tank cover plate | Muscle strain (~70 lbs lift hazard) | Must have 2 people to remove cover. Wear safety toe, non-slip shoes and durable work gloves. |
|  | Electrical: Work within crowbar tank. | 90 kV, 0.22 uF output cap | Use 1 dedicated Phenix discharge stick, rated for 100 kVDC, to soft ground and then hard ground the top of the 0.22 uF output capacitor. |
|  | Electrical: Work within the crowbar tank | 30 kV, 4 each: 8 uF filter caps 30 kV, 4 each: 0.24 uF SCR snubbers | Use 2 dedicated Phenix soft grounding discharge sticks to simultaneously ground across each of four bushing sets feeding the main tank. Use additional ground sticks to apply hard grounds. |
|  | Electrical: Work within the crowbar tank | Dielectric recharge 90 kV, 0.22 uF output cap | Bolt a shorting wire from the top of 0.22 uF output capacitor to ground. |
|  | Mechanical: Work in crowbar tank | Bumps, bruises, and strain. Exposure to high voltage oil. | Must have physical ability to safely perform the work. Removal of SCR stacks is particularly difficult. Requires foam/rubber pads, maintenance blankets. Use disposable nitrile gloves when handling oil-covered components. Note: should rotate stacks long ways to drain captured oil from them over tank before moving them to side. After removing stacks from the tank, place them in plastic parts bins lined with oil absorbent pads. Proper waste containers from Waste Management must be obtained before the start of work. All material used for handling oil-covered items, such as nitrile gloves, absorbent pads, wipes, etc., must be placed in these containers. |
|  | Mechanical: Transporting heavy or awkward parts to and from the top of the power supplies. | Strain and trip hazard carrying awkward/heavy items up and down the stairs from the top of the power supply. | The SSRL mechanical services group (MSG) has a lifting basket staged next to the HVPS. Bulky and/or awkward components that need to be transported to and from the top of the HVPS are lifted in the basket by a forklift operated by the MSG. Workers on the HVPS should coordinate the movement of these components with MSG. |

# Authorization

| Authorizer (administrative or functional supervisor, foreman, POC). I have reviewed the steps, hazards and controls described in this EWP. Workers are qualified (that is, licensed or certified, as appropriate, and in full compliance with SLAC training requirements) to perform this activity. |  |  |
| --- | --- | --- |
| Name (print): | Signature: | Date: |

# Release

| Area or building manager Red work? Yes. Document release via WIP and tailgate meeting. No. I have communicated unique area hazards, boundary conditions, and so on with the authorizer or listed worker(s) and have coordinated this job with affected occupants. Listed workers are released to perform described scope of work. |  |  |
| --- | --- | --- |
| List boundary conditions, notes, etc: |  |  |
| Name (print): | Signature: | Date: |

# Worker Acknowledgement (add rows as needed)

| Worker. I understand and will adhere to the steps, hazards, and controls in this EWP. I understand that performing steps out of sequence may pose hazards that have not been evaluated nor authorized. I will contact the person who authorized my work before continuing if the scope of work changes or new hazards are introduced. I understand my stop work authority and responsibility. |  |  |
| --- | --- | --- |
| Name (print) | Signature | Date |

# Electrical Work Procedure 
(optional: insert or attach procedure(s), LOTO energy isolation plan(s) and associated drawings/sketches below)

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]

## [Heading 2]

[Body Text]

### [Heading 3]

[Body Text]

### [Heading 3]

[Body Text]