## HVPS1
Log of HVPS1 events
Date | Description | Resource | Comment | Lost time (hrs) | Length of run | Failure/Swap
2005-11-08 | Replaced crowbar stacks | PEM elog | Annual maintenance
2005-11-15 | HVPS1 failing at 50 kV | PEM elog | Incorrect MCO relay setting (also two shorted caps in High B+ phase stack)
2006-06-23 | HVPS1 transformer arc trip | PEM elog, history | Tension rod snapped. Beam lost 06:00 on 06/23. Restored at 12:00 on 06/24. |  | 220 | F
2006-07-10 | HVPS1 crowbar stack replacement | PEM elog | Replaced existing stacks with those tested in the shop. Some existing stacks weak
2006-08-18 | HVPS1 C+ stack has truncated output? | PEM elog | Replaced high value snubber resistor. Was that an operational problem?
2007-03-09 | 60 Hz ripple | PEM elog | Tank opened, no problems found. No beam on Thursday or Friday. No documentation | 14
2007-04-21 | Removed phase stacks to continue 60 Hz troubleshooting | PEM elog | No obvious problem found, but layout of gate trigger wires not dressed as desired
2007-07-29 | Phase tank failure | PEM elog (Blankenship), history | One low side cap and stack shorted. Replaced all 6 stacks. Down at 06:00, up at 15:00 | 9 | 142 | F
2008-03-10 | Crowbar tank maintenance | PEM elog | One stack tension rod broken
2008-08-29 | PM on phase tank | PEM elog | One optical SCR did not properly fire
2009-05-19 | Crowbar tank swapout | PEM elog, history | Output cap failing, likely cause for trips, perhaps in AP? | 5 | 660 | F
2009-06-01 | Phase tank maintenance | PEM elog | Some failed redundant components. Good pictures of phase tank
2009-08-27 | Annual maintenance | PEM elog
2010-04-05 | Annual maintenance | PEM elog | Crowbar tank stack swap
2010-11-26 | Oil level gauge failed | PEM elog, ops elog, history | Verified oil level ok and bypassed gauge. Recovery from Thanksgiving | 6
2011-03-07 | Annual maintenance | PEM elog | Some failed redundant components.
2011-10-11 | Added oil to switchover tank | PEM elog
2012-10-23 | HVPS1 controller error | ops elog | Wanted to switch to HVPS1, but switchgear controller could not pass PPS certification
2012-10-26 | Switch to HVPS1 | ops elog | Switchgear controller repaired RSWCF 5567
2012-10-27 | HVPS1 failed. Tracking on glastic board in switchover tank running on HVPS1 | PEM elog, ops log | No failure in supply. Repair by removing glastic board. Good photos in ops 622431
2013-10-15 | Replace sontex oil with FR3 | rf elog
2013-10-25 | Switch to HVPS1 | PEM elog | Normal swap RSWCF 5985
2013-12-16 | HVPS2 failure; switch to HVPS1 | ops elog | RSWCF 6030
2014-01-13 | Maintenance on voltage divider during PAMM | PEM elog | radiator shorted out voltage divider
2015-10-15 | Switch to HVPS1 | ops elog | Normal swap RSWCF 6643 |  | 365 | S
2016-11-10 | Switch to HVPS1 | ops elog, history | HVPS2 failed RSWCF 7004 |  | 347 | S
2017-10-23 | Switch to HVPS1 | ops elog, history | HVPS2 failed RSWCF 7252 |  | 126 | S
2018-03-18 | Switch to HVPS1 | ops elog, history | HVPS2 failed RSWCF 7327 |  | 107 | F
2018-07-03 | HVPS1 failure | ops elog, history | failure during AP. Phase stacks all pass, but one stack, high side B+, has two failed stages so is replaced and repaired.
2018-07-08 | Switch to HVPS1 | ops elog, history | Found faulty ABB MCO relay on Phase C RSWCF 7410
2018-10-08 | HVPS1 failure | ops elog, history | Found faulty 90 kV HV output bushing failed due to overheating from resistive contact. Bushing and 500 ohm resistors replaced. | N/A Startup | N/A Startup
2018-10-15 | Switch to HVPS1 |  | Test repair for several days
2018-10-18 | Switch to HVPS2 |  | HVPS1 functioning properly before switch
2018-11-14 | Switch to HVPS1 |  | HVPS2 failed on high side phase stack C+
2018-11-26 | Switch to HVPS2 |  | HVPS1 functioning properly before switch
2018-02-28 | Switch to HVPS1 |  | This is the first maintenance opportunity for HVPS1 in several years since HVPS2 had not been proved to be reliable. The crowbar stacks were swapped out with tested good stacks as part of normal maintenance. Will report back when tests of removed SCRs are completed. This switch of the HVPS is to test out the operation of HVPS1 after the maintenance.
2020-01-06 | Switch to HVPS2 |  | HVPS1 functioning properly before switch; successfully passed infant mortality test
2020-08-17 | Start infant mortality test on refurbished HVPS2
2020-09-02 | Switch over to HVPS1 after HVPS2 failure
2020-09-29 | Switch to HVPS2 to test repairs |  | HVPS1 functioning properly before switch
2021-04-29 | Swap to HVPS1 to ensure it is functional |  | HVPS2 functioning properly before switch
2022-04-14 | Swap to HVPS2 for operation |  | HVPS1 functioning properly before switch
2022-08-03 | HVPS1 maintenance completed
2022-10-04 | Swap to HVPS1 for operation | Cater 157822, RSWCF 9032 | HVPS2 functioning properly before switch
2024-01-16 | Swap to HVPS2 for operation | Cater 166810, RSWCF 9576 | HVPS1 functioning properly before switch
2024-03-14 | Swap to HVPS1 for operation | Cater 169090, RSWCF 9705 | HVPS2 failed

## HVPS2
Log of HVPS2 (nee 8-3) events
Date | Description | Resource | Comment | Lost time (hrs) | Time to failure
2009-01-21 | work started on 8-3 prep | PEM elog
2010-04-15 | 8-3 prep | PEM elog
2011-06-08 | 8-3 final prep begins | PEM elog | Many entries omitted from this spreadsheet
2011-10-19 | Near final checkout of HVPS2 internals | PEM elog | Details of small fixes that were required
2012-06-12 | Work continues on HVPS2 installation | PEM elog
2012-08-29 | Work on HVPS2 nears completion | PEM elog | Stacks in both crowbar and phase tanks installed
2012-10-15 | Certify PPS | history
2012-10-16 | RF processing starts | history, ops elog
2012-10-21 | multiple HVPS trips | history, ops elog | Suspected loose banana plug in termination tank. Early part of spear startup
2012-10-22 | more HVPS trips | history, ops elog | Lower gap voltage to minimize trips. Suspect problems with HVPS2; switch over to HVPS1. RSWCF 5560
2012-10-23 | Tracking on glastic board in switchover tank running on HVPS2 | PEM elog | No failure in supply.
2012-10-27 | Tracking on glastic board in switchover tank running on HVPS1 | PEM elog | No failure in supply. Repair by removing glastic board.
2012-11-02 | Switch over to HVPS2 | ops elog | Verify HVPS2 works. RSWCF 5568
2013-09-19 | Run new 60' RG220 cable from HVPS2 to termination tank | PEM elog |  |  | 357
2013-12-10 | Switch over to HVPS2 | PEM elog | Lack of sufficient FR3 for HVPS1. Performed in maintenance day. RSWCF 6027
2013-12-16 | HVPS2 failure | ops elog, history | Happened during AP time, but extensive troubleshooting required | 4 | 6
2014-01-15 | HVPS2 troubleshooting | PEM elog | used variac on four output stages of HVPS to find problem with one stage. 697713 has photos of rectifier stacks
2014-01-28 | HVPS2 troubleshooting | PEM elog | Found HV bushing had failed on return line. Photographs in 699760
2014-01-31 | HVPS2 troubleshooting | PEM elog | Discovered rectifier stack 3 is shorted
2014-02-13 | HVPS2 repair | PEM elog | Cannibalized 8-5. Photos in 702943, 704165, 704513
2014-03-14 | HVPS2 repair | PEM elog | Repair complete except for installing new output cables
2014-04-07 | Switch over to HVPS2 | ops elog, history | Test repaired HVPS2 RSWCF 6114 |  | 556
2016-10-14 | Switch over to HVPS2 | RSWCF | Normal swap RSWCF 6946
2016-11-10 | HVPS2 failure | ops elog, history | Startup? | 10 | 27
2016-11-16 | HVPS2 repair begins | PEM elog | Note that HVPS2 is mislabeled in these entries as HVPS1. High side of A- phase stack failed catastrophically. The snubber resistor exploded and capacitor failed.
2016-12-03 | HVPS2 repair | PEM elog | Detailed pictures of snubber cap assemblies in 875839 Subsequent investigation found some open connections in local snubber circuitry
2017-03-28 | HVPS2 closed up | PEM elog
2017-09-22 | Switch over to HVPS2 | PEM elog | Normal swap RSWCF 6946
2017-10-23 | HVPS2 failure | ops elog, history | During startup | 7 | 31
2017-10-31 | HVPS2 repair begins | PEM elog | Crowbar and phase tanks appear ok
2017-11-08 | HVPS2 repair | PEM elog | suspect oil breakdown in switch tank
2017-12-13 | HVPS2 repair | PEM elog | suspect rectifier stack 3; larger leakage current than others
2017-12-15 | HVPS2 repair | PEM elog | Notice signs of arc between cable and busbar. (Don't see mention of failed high pot earlier that caused us to look for this failure.) Don't understand the high resistance measured between output cable and ground. Think that the cable should be grounded. Later thought this was just a measurement problem.
2017-12-16 | HVPS2 repair | PEM elog | Worried about capacitor 4's appearance. This may signify failure. Also a connection was loose. Pictures 922467
2017-12-19 | HVPS2 repair | PEM elog | Found resistors below value. Dressed main tank connections. Pictures 922881
2018-02-26 | Switch over to HVPS2 | ops elog | Test repaired HVPS2 RSWCF 6114
2018-03-18 | HVPS2 failure | ops elog |  | 6 | 20
2018-03-21 | HVPS2 repair | PEM elog | Found broken tension rod in crowbar stack 3. Checked all other stacks and replaced stack 3.
2018-07-03 | Switch over to HVPS2 | ops elog | HVPS1 failure RSWCF 7405
2018-07-06 | HVPS2 failure | ops elog, history | No problem found. Replaced all crowbar stacks and tried again | 12 | 3
2018-07-07 | HVPS2 failure | ops elog, history | Waiting for repair | 27 | 1
2018-10-07 | HVPS2 failure | ops elog, history | Found HV increasing in at least one case. Not an HV problem. Replaced AB DAC and regulator board | N/A Startup | N/A Startup
2018-10-10 | HVPS2 failure | ops elog, history | Oscilloscope captured enerpro error. Board swapped. | N/A Startup | N/A Startup
2018-10-10 | HVPS2 return to service |  | Test repaired HVPS2 for ~ five days before retesting HVPS1
2018-10-15 | Switch over to HVPS1 |  | HVPS2 functioning properly before switch
2018-10-18 | Switch over to HVPS2 |  | HVPS1 testing successful
2018-11-13 | HVPS2 failure |  | High side B-/C+ stack pair fires early at high voltage. C+ stack tested on the bench to have 7/13 failed devices that measured low resistances at voltages less than 4 kV
2018-11-26 | HVPS2 return to service |  | "New" high side bridge installed with 6 stacks tested in the shop to hold off 35 kV
2019-02-28 | Switch over to HVPS1 |  | HVPS2 functioning properly before switch
2020-01-06 | Switch over to HVPS2 |  | HVPS1 functioning properly before switch
2020-08-17 | Start infant mortality test on refurbished HVPS2 |  | Phase and crowbar tanks swapped out for normal maintenance
2020-09-02 | HVPS2 failure |  | High side (S2) B+ phase stack tension rod broken. Replaced this stack, but other damage had occurred. Rectifier 3 (50 kV - 75 kV) had damaged filter resistors. The filter rectifier in that section was also severly damaged. Phases A+ and C+ are shorted and B+ is open.
2020-09-29 | Switch over to HVPS2 to test repairs |  | HVPS1 functioning properly before switch
2021-04-29 | Swap to HVPS1 to ensure it is functional |  | HVPS2 functioning properly before switch
2022-04-14 | Swap to HVPS2 for operation |  | HVPS1 functioning properly before switch
2022-10-04 | Swap to HVPS1 for operation | Cater 157822, RSWCF 9032 | HVPS2 functioning properly before switch
2024-01-09 | Refurbish HVPS2 |  | Phase and crowbar tanks swapped out for normal maintenance after extended off time.
2024-01-16 | Swap to HVPS2 for operation | Cater 166810, RSWCF 9576 | HVPS1 functioning properly before switch
2024-03-13 | HVPS2 failure | elog 1263638; 1269729; 1270084; | Waveform from the inductor voltages show that the high side (S2) A+ phase triggers early. Waveform from HVPS output shows voltage dips when B+/A- and C+/A- thyristors fire. (elog 1263928). Two of the ceramic cases of the thyristors at the top of the A+ stack are discolored, possibly due to a water leak and/or overheating. The phase tank lid and associated radiator was replaced. In the shop, 6 of the 14 C- (B-?) stages had a very low resistance in both direction, few kOhms, so B- stack was breaking down.
2024-03-14 | Swap to HVPS1 for operation | Cater 169090, RSWCF 9705 | HVPS2 failed