## Stack Test jul062018
Spear 2 Crowbar Stack Testing |  | Test Date: 7/28/2018
Stacks removed July 06, 2018
All data @ 30 minutes | LC @ 25KV | Temps | Overvolts | Light
HV applied | mA | Deg. C | Self-Fire KV | Trigger
|  | Time= 30 mins | Pass/Fail | Pass/Fail
Crowbar 1 | 0.891+ | 28.2-32.4 | P43.3KV | Pass
Crowbar 2 | 0.862 | 28.4-35.2 | P 42.8KV | Pass
Crowbar 3 | 0.888 | 29.1-35.6 | P43.25KV | Pass
Crowbar 4 | 0.911+ | 28.2-37.9 | P 43.4KV | Pass
All 4 stacks removed from Spear 2 RF HVPS on July 6, 2018
Conclusions: Stack 4 has high leakage current (nominal should be < .890 mA) and is likely a culprit in sagging output volts. Stack 1 leakage current creaping upward slowly and is marginal. Stacks 2+3 appear to be good: leakage current was steady over 1/2 hour test period.

## Stack Test jul072018
Spear 2 Crowbar Stack Testing |  | Test Date: 8/4/2018
Stacks removed from Spear 2 August 03, 2018
All data @ 30 minutes | LC @ 25KV |  | Overvolts | Light
HV applied | mA |  | Self-Fire KV | Trigger
|  |  | Pass/Fail | Pass/Fail
Crowbar 1 | 0.857 | 1.12 mA | Failed @ 43KV | Pass
Crowbar 2 | 0.891 |  | Pass @ 43.55KV | Pass
Crowbar 3 | 0.861 |  | Pass @ 44.2 KV | Pass
Crowbar 4 | 0.887 |  | Pass @ 43.05 | Pass
Conclusions: Stack 1 functioned normally with good, stable leakage current. One SCR (#3 in stack 1) failed with self-fire @ 43 KV. The stack was good during ops. It is not normal for a stack to self-fire--the crowbar ckt operates with a trigger pulse. Leakage after failed SCR was 1.1 mA and stable @ 25KV. The other 5 SCRs in the stack are good. Stack 2 leakage @ 30 minutes was a little high, but appears to function correctly. Stacks 3+4 are good with stable leakage current @ 25 KVDC. It's possible over a longer operational period at higher temperatures in the crowbar tank than in free air the stacks started to partially self-fire (possibly stack 2). But from the uncertainty of this limited testing, it is warranted to test the main tank rectifiers and filter circuits and to replace the main tank rectifiers and filter caps and to perform a thorough inspection of wiring and bushings.

## Operational Data
Spear 2 RF HVPS Individual SCR Tests |  |  |  |  | 2018-08-08 |  |  |  | Spear 2 RF HVPS Individual SCR Tests |  |  |  |  | 2018-08-15
Set 2 Crowbar Stacks removed 3 August 2018 (failed 7 July 2018) | [8 empty] | Set 1 Crowbar Stacks removed 6 July 2018 (failed July 6 2018)
| SCR # | Serial # | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Creeping Up | Re-Use? |  | SCR # | Serial # | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Creeping Up | Re-Use? | Copied data for histograms (do not know how to histogram data from different columns)
[18 empty] | 4.2 kV | 6.5 kV | SelfFIre
Stack 1 | 1 | 2436 | 10.1 | 17.7 | Good | 7.7 | N | Yes | Stack 1 | 1 | 2326 | 154.2 | 495 | Good | 7.35 | Y | No | 10.1 | 17.7 | 7.7
| 2 | 2364 | 28.8 | 49.2 | Good | 7.3 | N | Yes |  | 2 | 2322 | 34.6 | 71 | Good | 7.8 | N | Yes | 28.8 | 49.2 | 7.3
| 3 | 2362 | 23.4 | 64.2 | Good | 0 | N | No |  | 3 | 2319 | 20.5 | 43 | Good | 0 | N | No | 23.4 | 64.2 | 0
| 4 | 2357 | 25.5 | 42.4 | Good | 7.3 | N | Yes |  | 4 | 2428 | 81.6 | 143.5 | Good | 7.8 | Y | No | 25.5 | 42.4 | 7.3
| 5 | 2361 | 11.6 | 21.5 | Good | 7.2 | N | Yes |  | 5 | 2429 | 99.3 | 276.5 | Good | 7.4 | Y | No | 11.6 | 21.5 | 7.2
| 6 | 5636 | 57.4 | 94.2 | Good | 7.5 | Y | No |  | 6 | 2350 | 9.3 | 24.7 | Good | 7.5 | N | Yes | 57.4 | 94.2 | 7.5
Stack 2 | 1 | 6219 | 51 | 416 | Good | 0 | N | No | Stack 2 | 1 | 3174 | 24.6 | 39.7 | Good | 7 | N | Yes | 51 | 416 | 0
| 2 | 6272 | 92 | 279 | Good | 7.72 | Y | No |  | 2 | 6230 | 45 | 85.7 | Good | 7.8 | Y | No | 92 | 279 | 7.72
| 3 | 6114 | 80 | 220 | Good | 7.75 | Y | No |  | 3 | 6234 | 11.3 | 26.7 | Good | 7.7 | N | Yes | 80 | 220 | 7.75
| 4 | 6217 | 41.8 | 181 | Good | 7.8 | N | Yes |  | 4 | 5000 | 29.9 | 97.7 | Good | 7.5 | N | Yes | 41.8 | 181 | 7.8
| 5 | 6171 | 26.4 | 61.8 | Good | 7.825 | N | Yes |  | 5 | 6235 | 18 | 32.3 | Good | 7.8 | N | Yes | 26.4 | 61.8 | 7.825
| 6 | 6227 | 11.8 | 28.8 | Good | 7.85 | N | Yes |  | 6 | 6228 | 21.9 | 46.2 | Good | 7.8 | N | Yes | 11.8 | 28.8 | 7.85
Stack 3 | 1 | 6285 | 97 | 195 | Good | 7.75 | N | Yes | Stack 3 | 1 | 6000 | 27.2 | 150 | Good | 7.7 | Y | No | 97 | 195 | 7.75
| 2 | 6222 | 42 | 140 | Good | 7.8 | Y | No |  | 2 | 6461 | 15 | 58.5 | Good | 7.6 | N | Yes | 42 | 140 | 7.8
| 3 | 6284 | 10.5 | 31.7 | Good | 7.75 | N | Yes |  | 3 | 6001 | 88.7 | 521 | Good | 7.7 | Y | No | 10.5 | 31.7 | 7.75
| 4 | 6287 | 13.2 | 34.5 | Good | 7.68 | N | Yes |  | 4 | 6002 | 16.1 | 72.6 | Good | 7.4 | N | Yes | 13.2 | 34.5 | 7.68
| 5 | 6286 | 29.2 | 162 | Good | 7.8 | N | Yes |  | 5 | 3292 | 32 | 79.5 | Good | 7.8 | N | Yes | 29.2 | 162 | 7.8
| 6 | 6220 | 15.7 | 31.5 | Good | 7.8 | N | Yes |  | 6 | 6003 | 63.4 | 127.8 | Good | 7.5 | Y | No | 15.7 | 31.5 | 7.8
Stack 4 | 1 | 6260 | 18.4 | 45 | Good | 7.75 | N | Yes | Stack 4 | 1 | 2731 | 18.5 | 62.6 | Good | 7.2 | N | Yes | 18.4 | 45 | 7.75
| 2 | 6264 | 101 | 286 | Good | 7.72 | Y | No |  | 2 | 3502 | 22.9 | 35.8 | Good | 7.2 | N | Yes | 101 | 286 | 7.72
| 3 | 6263 | 26.9 | 45.2 | Good | 7.7 | N | Yes |  | 3 | 3356 | 22.5 | 38.8 | Good | 7.6 | N | Yes | 26.9 | 45.2 | 7.7
| 4 | 6262 | 84.7 | 413 | Good | 7.7 | Y | No |  | 4 | 2874 | 20.4 | 51 | Good | 7 | N | Yes | 84.7 | 413 | 7.7
| 5 | 6294 | 29.3 | 162 | Good | 0 | N | No |  | 5 | 2969 | 366 | 633.2 | Good | 7.7 | Y | No | 29.3 | 162 | 0
| 6 | 3501 | 15.7 | 31.5 | Good | 0 | N | No |  | 6 | 2928 | 27.8 | 43.8 | Good | 7.6 | N | Yes | 15.7 | 31.5 | 0
[7 empty] | Num to reuse | 14 | [7 empty] | Num to reuse | 15 | 154.2 | 495 | 7.35
[18 empty] | 34.6 | 71 | 7.8
Note: Creeping Up = Y means current creeping upwards during measurement. Bad sign device will eventually | [8 empty] | Note: Creeping Up = Y means current creeping upwards during measurement. Bad sign device will eventually | [8 empty] | 20.5 | 43 | 0
break down under voltage in crowbar tank. |  |  |  | 0 in VBO test means a failure to self-fire |  |  |  |  | break down under voltage in crowbar tank. |  |  |  | 0 in VBO test means a failure to self-fire |  |  |  |  | 81.6 | 143.5 | 7.8
[18 empty] | 99.3 | 276.5 | 7.4
|  |  | Conclusions | [9 empty] | Conclusions |  |  |  |  | 9.3 | 24.7 | 7.5
[18 empty] | 24.6 | 39.7 | 7
Stacks 2 + 4 were bad. Believe these 2 be the culprit in the second Spear 2 failure (< 2 days run time). | [8 empty] | Stack 1 had 3 SCRs with high leakage current and a 4th SCR that failed on over-volts self-fire. | [8 empty] | 45 | 85.7 | 7.8
Stack 4 had 4 devices marginal or failed at self-fire (permanent short with one shot). | [8 empty] | Stack 3 has 3 SCRs with high leakage current. Both stack 1 + 3 indicate likely strong candidates for | [8 empty] | 11.3 | 26.7 | 7.7
[9 empty] | Spear 2 failure on July 06, 2018. | [8 empty] | 29.9 | 97.7 | 7.5
Stacks 1 + 3 are decent--not great though. Overall, found 10 devices out of 24 either marginal or failed. | [17 empty] | 18 | 32.3 | 7.8
[9 empty] | Stacks 2 + 4 are reasonably good. | [8 empty] | 21.9 | 46.2 | 7.8
It is apparent the previous 2 failures were due to crowbar stack failures. At this point, will construct and test | [17 empty] | 27.2 | 150 | 7.7
best possible stacks with each device tested for leakage, fiber optic triggering and ability to withstand | [8 empty] | It strongly appears both sets of crowbar stacks installed in Spear 2 led to the failures seen on Spear 2 over | [8 empty] | 15 | 58.5 | 7.6
over-voltage self-firing. Testing the whole stack and calling that stack good is obviously not the way to go. | [8 empty] | the short run times due to the inability of at least 2 stacks in each set being unable to hold off the | [8 empty] | 88.7 | 521 | 7.7
Previously, we tested the whole stack--it the overall leakage was under .890 and stable and passed trigger | [8 empty] | necessary voltage to allow full power supply output. | [8 empty] | 16.1 | 72.6 | 7.4
testing, we declared it good. From now on, we will test each device thoroughly and individually and use | [17 empty] | 32 | 79.5 | 7.8
the whole stack tests after a stack is assembled to make sure it works as a unit. | [17 empty] | 63.4 | 127.8 | 7.5
[18 empty] | 18.5 | 62.6 | 7.2
[18 empty] | 22.9 | 35.8 | 7.2
[18 empty] | 22.5 | 38.8 | 7.6
[18 empty] | 20.4 | 51 | 7
[18 empty] | 366 | 633.2 | 7.7
[18 empty] | 27.8 | 43.8 | 7.6
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Spares Data
Spare SCR tests to rebuild Spear 2 Crowbar Stacks.
2018-08-11
Spare # | Serial # | uA @ 4.2 KV | uA @ 6.5 KV | Fiber Optic | OV Self-Fire | Creeping Up | Good/Bad
1 | 5654 | 32.7 | 66.4 | Pass | 7.8 | Y | Bad
2 | 5640 | 11.6 | 40.2 | Pass | 7.75 | N | Good
3 | 2363 | 23.3 | 37.8 | Pass | 7.1 | N | Good
4 | 6224 | 13.8 | 30.1 | Pass | 7.795 | N | Good
5 | 3359 | 10.6 | 17.5 | Pass | 7.05 | N | Good
6 | 3381 | 15.4 | 42.1 | Pass | 6.95 | Y | Marginal
7 | 3175 | 9.8 | 16.6 | Pass | 7 | N | Good
8 | 2998 | 11.4 | 45.6 | Pass | 7.1 | Y | Marginal
9 | 6279 | 10.7 | 20.5 | Pass | 7.8 | N | Good
10 | 2360 | 8.7 | 16.2 | Pass | 7 | N | Good
11 | 3186 | 25.2 | 47.2 | Pass | 7 | N | Good
12 | 3360 | 4.5 | 9.5 | Pass | 7 | N | Good
13 | 3219 | 20.5 | 40.1 | Pass | 7.4 | Y | Marginal
14 | 3172 | 84.3 | 138.1 | Pass | 7.2 | Y | Marginal
15 | 5653 | 6.2 | 15 | Pass | 7.45 | N | Good
16 | 6234 | 11.1 | 24.4 | Pass | 7.8 | N | Good
17 | 6239 | 9.5 | 18.8 | Pass | 7.6 | N | Good
18 | 6244 | 6.7 | 19.6 | Pass | 7.6 | N | Good
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
[6 empty] | Num Good | 13
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Summary Data for Graphics
|  | Serial # | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Creeping Up | Re-Use? | # good dev | # bad dev | # marginal
Set 2 | Stack 1 | 2436 | 10.1 | 17.7 | Good | 7.7 | N | Yes | 42 | 20 | 4
|  | 2364 | 28.8 | 49.2 | Good | 7.3 | N | Yes
|  | 2362 | 23.4 | 64.2 | Good | 0 | N | No
|  | 2357 | 25.5 | 42.4 | Good | 7.3 | N | Yes
|  | 2361 | 11.6 | 21.5 | Good | 7.2 | N | Yes
|  | 5636 | 57.4 | 94.2 | Good | 7.5 | Y | No
| Stack 2 | 6219 | 51 | 416 | Good | 0 | N | No
|  | 6272 | 92 | 279 | Good | 7.72 | Y | No
|  | 6114 | 80 | 220 | Good | 7.75 | Y | No
|  | 6217 | 41.8 | 181 | Good | 7.8 | N | Yes
|  | 6171 | 26.4 | 61.8 | Good | 7.825 | N | Yes
|  | 6227 | 11.8 | 28.8 | Good | 7.85 | N | Yes
| Stack 3 | 6285 | 97 | 195 | Good | 7.75 | N | Yes
|  | 6222 | 42 | 140 | Good | 7.8 | Y | No
|  | 6284 | 10.5 | 31.7 | Good | 7.75 | N | Yes
|  | 6287 | 13.2 | 34.5 | Good | 7.68 | N | Yes
|  | 6286 | 29.2 | 162 | Good | 7.8 | N | Yes
|  | 6220 | 15.7 | 31.5 | Good | 7.8 | N | Yes
| Stack 4 | 6260 | 18.4 | 45 | Good | 7.75 | N | Yes
|  | 6264 | 101 | 286 | Good | 7.72 | Y | No
|  | 6263 | 26.9 | 45.2 | Good | 7.7 | N | Yes
|  | 6262 | 84.7 | 413 | Good | 7.7 | Y | No
|  | 6294 | 29.3 | 162 | Good | 0 | N | No
|  | 3501 | 15.7 | 31.5 | Good | 0 | N | No
Set 1 | Stack 1 | 2326 | 154.2 | 495 | Good | 7.35 | Y | No
|  | 2322 | 34.6 | 71 | Good | 7.8 | N | Yes
|  | 2319 | 20.5 | 43 | Good | 0 | N | No
|  | 2428 | 81.6 | 143.5 | Good | 7.8 | Y | No
|  | 2429 | 99.3 | 276.5 | Good | 7.4 | Y | No
|  | 2350 | 9.3 | 24.7 | Good | 7.5 | N | Yes
| Stack 2 | 3174 | 24.6 | 39.7 | Good | 7 | N | Yes
|  | 6230 | 45 | 85.7 | Good | 7.8 | Y | No
|  | 6234 | 11.3 | 26.7 | Good | 7.7 | N | Yes
|  | 5000 | 29.9 | 97.7 | Good | 7.5 | N | Yes
|  | 6235 | 18 | 32.3 | Good | 7.8 | N | Yes
|  | 6228 | 21.9 | 46.2 | Good | 7.8 | N | Yes
| Stack 3 | 6000 | 27.2 | 150 | Good | 7.7 | Y | No
|  | 6461 | 15 | 58.5 | Good | 7.6 | N | Yes
|  | 6001 | 88.7 | 521 | Good | 7.7 | Y | No
|  | 6002 | 16.1 | 72.6 | Good | 7.4 | N | Yes
|  | 3292 | 32 | 79.5 | Good | 7.8 | N | Yes
|  | 6003 | 63.4 | 127.8 | Good | 7.5 | Y | No
| Stack 4 | 2731 | 18.5 | 62.6 | Good | 7.2 | N | Yes
|  | 3502 | 22.9 | 35.8 | Good | 7.2 | N | Yes
|  | 3356 | 22.5 | 38.8 | Good | 7.6 | N | Yes
|  | 2874 | 20.4 | 51 | Good | 7 | N | Yes
|  | 2969 | 366 | 633.2 | Good | 7.7 | Y | No
|  | 2928 | 27.8 | 43.8 | Good | 7.6 | N | Yes
Spares |  | 5654 | 32.7 | 66.4 | Pass | 7.8 | Y | Bad
|  | 5640 | 11.6 | 40.2 | Pass | 7.75 | N | Good
|  | 2363 | 23.3 | 37.8 | Pass | 7.1 | N | Good
|  | 6224 | 13.8 | 30.1 | Pass | 7.795 | N | Good
|  | 3359 | 10.6 | 17.5 | Pass | 7.05 | N | Good
|  | 3381 | 15.4 | 42.1 | Pass | 6.95 | Y | Marginal
|  | 3175 | 9.8 | 16.6 | Pass | 7 | N | Good
|  | 2998 | 11.4 | 45.6 | Pass | 7.1 | Y | Marginal
|  | 6279 | 10.7 | 20.5 | Pass | 7.8 | N | Good
|  | 2360 | 8.7 | 16.2 | Pass | 7 | N | Good
|  | 3186 | 25.2 | 47.2 | Pass | 7 | N | Good
|  | 3360 | 4.5 | 9.5 | Pass | 7 | N | Good
|  | 3219 | 20.5 | 40.1 | Pass | 7.4 | Y | Marginal
|  | 3172 | 84.3 | 138.1 | Pass | 7.2 | Y | Marginal
|  | 5653 | 6.2 | 15 | Pass | 7.45 | N | Good
|  | 6234 | 11.1 | 24.4 | Pass | 7.8 | N | Good
|  | 6239 | 9.5 | 18.8 | Pass | 7.6 | N | Good
|  | 6244 | 6.7 | 19.6 | Pass | 7.6 | N | Good
|  | mean | 38.3348 | 105.3864 |  | 7.5285
|  | std | 29.6275 | 92.1862
|  | ratios | mean | 2.7491
|  |  | std | 3.1115
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
mean = 38.3
std = 29.6
mean = 105.4
std = 92.2

## Replacement Stacks 1
New Set of Crowbar Stacks for Spear 2 RF HVPS 18 Aug 2018
Stack 1 | SCR S/N | Stack Leakage @ 25 KVDC | Fiber Optic Trig Test | Pass/Fail | Old #
Cell 1 | 6239
Cell 2 | 3359
Cell 3 | 6461 | 0.846 uA | Pass | Pass | 0.85
Cell 4 | 6279
Cell 5 | 3175
Cell 6 | 2350
Stack 2
Cell 1 | 2360
Cell 2 | 2322
Cell 3 | 3502 | .859 uA | Pass | Pass
Cell 4 | 2731
Cell 5 | 3186
Cell 6 | 5653
Stack 3
Cell 1 | 6239
Cell 2 | 2361
Cell 3 | 2874 | .848 uA | Pass | Pass | 0.868
Cell 4 | 3292
Cell 5 | 2436
Cell 6 | 6244
Stack 4
Cell 1 | 6234
Cell 2 | 3356
Cell 3 | 5000 | .851 uA | Pass | Pass
Cell 4 | 6220
Cell 5 | 6284
Cell 6 | 3360

## Replacement Stacks 2
Ohm Tests for New Spear 2 Crowbar Stacks | [7 empty] | 2018-08-21 |  |  |  |  | Ohm Tests for New Spear 2 Crowbar Stacks | [7 empty] | 2018-08-21
[8 empty] | Updated | [12 empty] | Updated
Fwd Direction |  | Ohms (Meas) | Volts | Current | Ohms (Calc) | LTT Current | LTT Ohms (Calc) | 2018-08-22 |  |  |  |  | Reverse Direction |  | Ohms (Meas) | Volts | Current | Ohms (Calc) | LTT Current | LTT Ohms (Calc) | 2018-08-22
|  | M Ohms |  | mA | M Ohms | uA | M Ohms | [7 empty] | M Ohms |  | mA | M Ohms | uA | M Ohms
[10 empty] | Old #s | [12 empty] | Old #s
Stack 1 | Replace S/N | 29.3 | 10488 | 0.355 | 29.5437 |  |  |  | 27.3 | 10489 | 0.394 | 26.6218 | Stack 1 | Replace S/N | 29.5 | 10488 | 0.356 | 29.4607 |  |  |  | 27.4 | 10489 | 0.383 | 27.3864
1 |  | 4.78 | 5233 | 1.09 | 4.8009 | 43.4 | 120.576 | [5 empty] | 1 |  | 4.79 | 5232 | 1.09 | 4.8 | 43.6 | 120
2 | 3359 | 4.98 | 5234 | 1.05 | 4.9848 | 3.2 | 1635.625 |  | 4.7 | 5232 | 1.11 | 4.7135 | 2 | 3359 | 4.99 | 5235 | 1.05 | 4.9857 | 3 | 1745 |  | 4.5 | 5231 | 1.16 | 4.5095
3 |  | 4.76 | 5232 | 1.1 | 4.7564 | 53.6 | 97.6119 | [5 empty] | 3 |  | 4.67 | 5231 | 1.12 | 4.6705 | 73.8 | 70.8808
4 | 6279 | 4.96 | 5233 | 1.06 | 4.9368 | 13.4 | 390.5224 |  | 4.7 | 5232 | 1.11 | 4.7135 | 4 | 6279 | 4.92 | 5235 | 1.07 | 4.8925 | 23 | 227.6087 |  | 4.81 | 5232 | 1.09 | 4.8
5 | 3175 | 4.92 | 5233 | 1.06 | 4.9368 | 13.4 | 390.5224 |  | 4.55 | 5231 | 1.15 | 4.5487 | 5 | 3175 | 4.92 | 5234 | 1.06 | 4.9377 | 13.2 | 396.5152 |  | 4.19 | 5230 | 1.25 | 4.184
6 |  | 4.9 | 5232 | 1.07 | 4.8897 | 23.6 | 221.6949 |  | Replaced SCRs 2,4, 5 in stack 1. |  |  |  | 6 |  | 4.87 | 5233 | 1.09 | 4.8009 | 43.4 | 120.576 |  | Replaced SCRs 2,4, 5 in stack 1.
| Total | 29.3 | AVG: | 1.0717 | 29.3053 |  |  |  | Test results updated. |  |  |  |  | Total | 29.16 | AVG: | 1.08 | 29.0874 |  |  |  | Test results updated.
Stack 2 |  | 29.3 | 10491 | 0.358 | 29.3045 | [7 empty] | Stack 2 |  | 29.3 | 10490 | 0.358 | 29.3017
1 |  | 4.94 | 5234 | 1.06 | 4.9377 | 13.2 | 396.5152 | [5 empty] | 1 |  | 4.95 | 5234 | 1.06 | 4.9377 | 13.2 | 396.5152
2 |  | 4.75 | 5233 | 1.1 | 4.7573 | 53.4 | 97.9963 | [5 empty] | 2 |  | 4.84 | 5233 | 1.08 | 4.8454 | 33.4 | 156.6766
3 |  | 4.9 | 5235 | 1.07 | 4.8925 | 23 | 227.6087 | [5 empty] | 3 |  | 4.91 | 5234 | 1.07 | 4.8916 | 23.2 | 225.6034
4 |  | 4.89 | 5235 | 1.07 | 4.8925 | 23 | 227.6087 | [5 empty] | 4 |  | 4.89 | 5234 | 1.07 | 4.8916 | 23.2 | 225.6034
5 |  | 4.85 | 5233 | 1.08 | 4.8454 | 33.4 | 156.6766 | [5 empty] | 5 |  | 4.85 | 5233 | 1.08 | 4.8454 | 33.4 | 156.6766
6 |  | 4.97 | 5235 | 1.05 | 4.9857 | 3 | 1745 | [5 empty] | 6 |  | 4.96 | 5234 | 1.06 | 4.9377 | 13.2 | 396.5152
| Total | 29.3 | AVG: | 1.0717 | 29.3111 | [8 empty] | Total | 29.4 | AVG: | 1.07 | 29.3494
[10 empty] | Old #'s | [12 empty] | Old #'s
Stack 3 |  | 29.5 | 10495 | 0.356 | 29.4803 |  |  |  | 28.1 | 10489 | 0.374 | 28.0455 | Stack 3 |  | 29.4 | 10494 | 0.357 | 29.395 |  |  |  | 27.9 | 10491 | 0.376 | 27.9016
1 |  | 4.96 | 5235 | 1.06 | 4.9387 | 13 | 402.6923 | [5 empty] | 1 |  | 4.89 | 5234 | 1.07 | 4.8916 | 23.2 | 225.6034
2 | 2361 | 4.97 | 5235 | 1.05 | 4.9857 | 3 | 1745 |  | 4.5 | 5232 | 1.16 | 4.5103 | 2 |  | 4.67 | 5233 | 1.12 | 4.6723 | 73.4 | 71.2943 |  | 4.67 | 5233 | 1.12 | 4.6723
3 |  | 4.78 | 5233 | 1.1 | 4.7573 | 53.4 | 97.9963 | [5 empty] | 3 |  | 4.96 | 5235 | 1.06 | 4.9387 | 13 | 402.6923
4 |  | 4.84 | 5233 | 1.08 | 4.8454 | 33.4 | 156.6766 | [5 empty] | 4 |  | 4.65 | 5232 | 1.13 | 4.6301 | 83.6 | 62.5837
5 | 2436 | 4.97 | 5235 | 1.05 | 4.9857 | 3 | 1745 |  | 4.65 | 5232 | 1.12 | 4.6714 | 5 |  | 4.8 | 5233 | 1.05 | 4.9838 | 3.4 | 1539.1176 |  | 4.8 | 5233 | 1.09 | 4.8009
6 |  | 4.94 | 5234 | 1.06 | 4.9377 | 13.2 | 396.5152 |  | Replaced SCRs 2 + 5. Test results |  |  |  | 6 |  | 4.87 | 5233 | 1.07 | 4.8907 | 23.4 | 223.6325 |  | Replaced SCRs 2 + 5. Test results
| Total | 29.46 | AVG: | 1.0667 | 29.4505 |  |  |  | updated. |  |  |  |  | Total | 28.84 | AVG: | 1.0833 | 29.0071 |  |  |  | updated.
Stack 4 |  | 29.5 | 10493 | 0.355 | 29.5577 | [7 empty] | Stack 4 |  | 27.7 | 10489 | 0.378 | 27.7487
1 |  | 4.92 | 5235 | 1.06 | 4.9387 | 13 | 402.6923 | [5 empty] | 1 |  | 4.88 | 5234 | 1.07 | 4.8916 | 23.2 | 225.6034
2 |  | 4.92 | 5235 | 1.06 | 4.9387 | 13 | 402.6923 | [5 empty] | 2 |  | 4.92 | 5235 | 1.06 | 4.9387 | 13 | 402.6923
3 |  | 4.83 | 5234 | 1.08 | 4.8463 | 33.2 | 157.6506 | [5 empty] | 3 |  | 4.75 | 5233 | 1.1 | 4.7573 | 53.4 | 97.9963
4 |  | 4.91 | 5235 | 1.07 | 4.8925 | 23 | 227.6087 | [5 empty] | 4 |  | 4.82 | 5234 | 1.08 | 4.8463 | 33.2 | 157.6506
5 |  | 4.95 | 5236 | 1.06 | 4.9396 | 12.8 | 409.0625 | [5 empty] | 5 |  | 4.71 | 5233 | 1.11 | 4.7144 | 63.4 | 82.5394
6 |  | 4.98 | 5236 | 1.05 | 4.9867 | 2.8 | 1870 | [5 empty] | 6 |  | 4.98 | 5235 | 1.05 | 4.9857 | 3 | 1745
| Total | 29.51 | AVG: | 1.0633 | 29.5425 | [8 empty] | Total | 29.06 | AVG: | 1.0783 | 29.134
All tests performed with Fluke 1555 10KV insulation tester. Stack test current measured in uA. Each individual device measured in mA with a 5 meg ohm, 5 watt, 1% resistor in parallel with the device.

## Temperature Dependence
Preliminary Temperature Dependence Tests
S/N | Temp degC | uA @ 4.2 KV | uA @ 6.5KV
6235 | 32.9 | 32.5 | 50.9
| 49 | 41.7 | 68.3
| 54 | 44.1 | 72.7

## infineon devices for test
2018-08-31
SCRs sent to Infineon for analysis
Number | S/N | Date Code |  | copy of results from testing | [6 empty] | Set | Stack | Infineon report
1 | 2969 | 26R9 |  | 2969 | 366 | 633.2 | Good | 7.7 | Y | No | 1 | 4 | P01 |  | spare |  | ok
2 | 6001 | 20U9 |  | 6001 | 88.7 | 521 | Good | 7.7 | Y | No | 1 | 3 | P02 |  | spare |  | ok
3 | 3501 | 25S5 |  | 3501 | 15.7 | 31.5 | Good | 0 | N | No | 2 | 4 | P03 |  | 1 | 1 | ok
4 | 6114 | 20U9 |  | 6114 | 80 | 220 | Good | 7.75 | Y | No | 2 | 2 | P04 |  | 2 | 4 | reduced blocking in forward and reverse directions
5 | 6294 | 20U9 |  | 6294 | 29.3 | 162 | Good | 0 | N | No | 2 | 4 | P05 | 6001 | 1 | 3 | ok
6 | 2429 | 13R2 |  | 2429 | 99.3 | 276.5 | Good | 7.4 | Y | No | 1 | 1 | P06 |  | 2 | 2 | shorted forward, reduced blocking reversed
7 | 2319 | ? |  | 2319 | 20.5 | 43 | Good | 0 | N | No | 1 | 1 | P07 |  | 2 | 2 | ok
8 | 6219 | 20U9 |  | 6219 | 51 | 416 | Good | 0 | N | No | 2 | 2 | P08 |  | 2 | 2 | ok
9 | 6272 | 20U9 |  | 6272 | 92 | 279 | Good | 7.72 | Y | No | 2 | 2 | P09 | 2969 | 1 | 4 | forward blocking peculiarity at 2000 V
10 | 2326 | ? |  | 2326 | 154.2 | 495 | Good | 7.35 | Y | No | 1 | 1 | P10 |  | 2 | 4 | reduced blocking in forward and reverse directions
11 | 6225 | 20U9 | [10 empty] | P11 |  | 1 | 1 | reduced blocking in forward and reverse directions
12 | 6223 | 20U9 | [10 empty] | P12 |  | 1 | 1 | ok
SCRs 11 + 12 are tested out of box, but unused in field.

## high-pot results
Spear 2 RF HVPS Hipot Test Results |  |  |  |  | 16 Aug 2018 + 24 Aug 2018 |  | Spear 2 RF HVPS Hipot Test Results |  |  |  |  | 7 Sept. 2018
2018-08-16 |  | Volts KV | Leakage I | Start/Stop | Resistance |  |  |  | Volts KV | Leakage I | Start/Stop | Resistance
|  |  | mA |  | MΩ |  |  |  |  | mA |  | MΩ
Stage 1 | Begin | 25.5 | 5.2 | 1142 | 4.9038 |  | Stage 1 | Begin | 25.5 | 5.85 | 0940 | 4.359
| 10 mins. | 26 | 5.2 | 1152 | 5 |  |  | 5 mins. | 25.3 | 5.82 | 0945 | 4.3471
Stage 2 | Begin | 25 | 4.6 | 1158 | 5.4348 |  | Stage 2 | Begin | 25.2 | 5.25 | 0954 | 4.8
| 10 mins. | 25.8 | 4.6 | 1208 | 5.6087 |  |  | 5 mins. | 25.1 | 5.23 | 0959 | 4.7992
Stage 3 | Begin | 25 | 6.6 | 1214 | 3.7879 |  | Stage 3 | Begin | 25.4 | 4.33 | 1006 | 5.8661
| 10 mins. | 25.5 | 6.55 | 1225 | 3.8931 |  |  | 5 mins. | 25.4 | 4.32 | 1011 | 5.8796
Stage 4 | Begin | 16 | 3 | 1227 | 5.3333 |  | Stage 4 | Begin | 16.1 | 3.5 | 1017 | 4.6
| 10 mins. | 16 | 3 | 1237 | 5.3333 |  |  | 5 mins. | 16 | 3.5 | 1022 | 4.5714
Stage 1 to Stage 3: | [6 empty] | Stage 1 to Stage 3:
| Not performed. | [6 empty] | Begin | 80.5 | 4.85 | 1057 | 16.5979 | 15.025
[8 empty] | 10 mins. | 80.5 | 4.7 | 1107 | 17.1277 | 15.0259
2018-08-24
Stage 1 to Stage 4: | [6 empty] | Stage 1 to Stage 4:
| Begin | 81.5 | 4.2 | 1120 | 19.4048 | 19.4598 |  | Begin | 89 | 4 | 1120 | 22.25 | 19.625
| 10 mins. | 80.5 | 4.15 | 1130 | 19.3976 | 19.8352 |  | 10 mins. | 89 | 4 | 1130 | 22.25 | 19.5974
Supply hipot testing performed with crowbar stacks and crowbar snubber resistors removed.
Hipot test set used (High Voltage Inc. 130 KVDC, 10 mA) has analog volt and current meters.
Supply hipot testing performed after newly rebuilt crowbar stacks installed and 13 main tank rectifier filter/current limiting resistors changed out (32 resistors total in tank). Crowbar snubber resistors installed. The 500 ohm filter resistors were out of tolerance band (450-550 ohms) either high or low (mostly low). Stage 3 rectifier swapped with spare from building 725. Hipot set for individual stages = Phenix Technologies 40 KVDC, 20 mA with digital voltage and current meters. Overall and stage 1-3 tests done with same hipotter as used on 24 Aug 2018.

## rectifier high-pot results
Test of Spear 2 RF HVPS Main Rectifier Stack #3 vs Spare Main Rectifier Stack
from Building 725
[8 empty] | 8 Sept. 2018 |  |  |  |  | 8 Sept. 2018
Hipot leakage currents stage to stage from August 16, 2018 | [5 empty] | Spare Main Rectifier Diode Stack and Filter Box Diode Hipot Tests |  |  |  |  | Spear 2 RF HVPS Main Rectifier Diode Stack and Filter Box Diode Hipot Tests
|  | Volts KV | Leakage I | Start/Stop |  | Neg Rail | Volts | Leakage I | Dwell Time |  | Neg Rail | Volts | Leakage I | Dwell time
|  |  | mA |  | MW |  | KV | mA |  | MW |  | KV | mA |  | MW
Stage 1 | Begin | 25.5 | 5.2 | 1142 | 4.9038 | A- | 25 | 4.7 | 1 Min. | 5.3191 | A- | 25 | 7.32 | 1 Min. | 3.4153
| 10 mins. | 26 | 5.2 | 1152 | 5 | B- | 25 | 4.9 | 1 Min. | 5.102 | B- | 25 | 8.04 | 1 Min. | 3.1095
[6 empty] | C- | 25 | 4.7 | 1 Min. | 5.3191 | C- | 25 | 7.38 | 1 Min. | 3.3875
Stage 2 | Begin | 25 | 4.6 | 1158 | 5.4348
| 10 mins. | 25.8 | 4.6 | 1208 | 5.6087 | Pos Rail | Volts | Leakage I | Dwell Time |  | Pos Rail | Volts | Leakage I | Dwell Time
[7 empty] | KV | mA |  |  |  | KV | mA
Stage 3 | Begin | 25 | 6.6 | 1214 | 3.7879 | A+ | 25 | 4.9 | 1 Min. | 5.102 | A+ | 25 | 7.45 | 1 Min. | 3.3557
| 10 mins. | 25.5 | 6.55 | 1225 | 3.8931 | B+ | 25 | 5.3 | 1 Min. | 4.717 | B+ | 25 | 7.4 | 1 Min. | 3.3784
[6 empty] | C+ | 25 | 4.9 | 1 Min. | 5.102 | C+ | 25 | 7.95 | 1 Min. | 3.1447
Stage 4 | Begin | 16 | 3 | 1227 | 5.3333
| 10 mins. | 16 | 3 | 1237 | 5.3333 |  | Filter Box Diodes, Spare Stack |  |  |  |  | Filter Box Diodes, #3 Rectifier Stack
[6 empty] | Neg Rail | Volts | Leakage I | Dwell Time |  | Neg Rail | Volts | Leakage I | Dwell Time
[7 empty] | KV | uA |  | MW |  | KV | uA |  | MW
[6 empty] | A- | 10 | 86 | 1 Min. | 116.2791 | A- | 10 | 82 | 1 Min. | 121.9512
[6 empty] | B- | 10 | 85 | 1 Min. | 117.6471 | B- | 10 | 74 | 1 Min. | 135.1351
[6 empty] | C- | 10 | 85 | 1 Min. | 117.6471 | C- | 10 | 73 | 1 Min. | 136.9863
[6 empty] | Pos Rail | Volts | Leakage I | Dwell Time |  | Pos Rail | Volts | Leakage I | Dwell Time
[7 empty] | KV | uA |  |  |  | KV | uA
[6 empty] | A+ | 10 | 95 | 1 Min. | 105.2632 | A+ | 10 | 77.5 | 1 Min. | 129.0323
[6 empty] | B+ | 10 | 88 | 1 Min. | 113.6364 | B+ | 10 | 80.2 | 1 Min. | 124.6883
[6 empty] | C+ | 10 | 86 | 1 Min. | 116.2791 | C+ | 10 | 81 | 1 Min. | 123.4568
Conclusions: Keep in mind, main rectifier stack 3 from Spear 2 suffered a fully shorted stack during the failure of the return bushing in 2016. We also replaced the filter cap across stack 3 as a precaution. The other 5 main rectifier stacks and the filter box stacks in #3 were basically ohmed and diode checked at low volts/amps--not checked at HV except during the thru-wall test at 25 KV. The stage test does not check each stack individually--but, as you can see from the left hand chart, stack 3 shows leakage current well above the 1st two identical stages (26 KV each). As you can see from the right-most chart, all 6 diode stacks are weak with high leakage compared both to the spare stack (middle chart) and the overall leakages seen for stacks 1 + 2 during the stage to stage hipots.
We have a smoking gun explanation now as to why we see higher leakage current on stack 3 overall and why the leakage current with new stack installed in the #3 main rectifier location in the main tank is much lower now (approx. 2 mA less). In the future, if we see leakages above 6 mA on any stage (perhaps 4 mA on stage 4), we should replace that stack. It maybe stack 3 would have functioned normally for a long time to come with higher reverse diode leakage, but it might be best to just change it out. But that decision is "above my pay grade".
Note: hipot tests done on spare and #3 main rectifier stacks performed with 500 ohm current limiting filter resistors removed to isolate filter box diode cards from main rectifier diode stacks.
Note: tested filter box diodes @ 10 KV in free air. Attempted 20 KV on the pos. side of spare box "C" phase: current climbed and I could smell pretty rapid heating of oil sheen on components. Tested this side again @ 10 KV and did low volts diode tests again to make sure no devices shorted. It appears there are probably air gap standoff issues as well with the cards so close together. The main rectifier stacks are rated @ 57 KVDC, but the standoff of the filter box diodes and RC's is unknown to me. I felt it would be safest to the filter box components to test at 10 KV. The comparison of reverse leakage currents between spare stack filter boxes and #3's leakage currents are similar. Keep in mind, these components are OLD and we don't have a tolerance band except on the snubber resistors (5%).

## desy thyristor leakageI
DESY Infineon T1503NH 75T S02
Blocking current (uA) at 4000 VDC 50 degC
Series 1 | Series 2 | Series 3.1 | Series 3.2 | Summary
400 | 130 | 220 | 230 | 400 | mean | 225.9167
300 | 300 | 230 | 230 | 300 | std | 62.4028
400 | 280 | 260 | 210 | 400
200 | 150 | 290 | 225 | 200
250 | 150 | 375 | 200 | 250
180 | 100 | 240 | 525 | 180
205 | 150 | 360 | 140 | 205
200 | 180 | 250 | 140 | 200
205 | 450 | 255 | 250 | 205
200 | 100 | 270 | 150 | 200
220 | 150 | 270 | 160 | 220
180 | 120 | 150 | 160 | 180
160 | 220 | 175 | 320 | 160
190 | 260 | 175 | 150 | 190
|  | 185 | 295 | 130
|  | 205 | 230 | 300
280
235 | 195.7143 | 244.375 | 225.9375 | 150
58.5714 | 75.9184 | 46.875 | 62.3047 | 150
100
150
180
450
100
150
120
220
260
220
230
260
290
375
240
360
250
255
270
270
150
175
175
185
205
230
230
210
225
200
525
140
140
250
150
160
160
320
150
295
230
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
mean = 225
std = 62

## ler 4-4
Leakage Tests of SCRs Removed From LER 4-4 (Sept. 13-14, 2018) + 2 Stacks From Spear 2 (Oct. 26, 2012)
Spear 2 Crowbar Stack removed Oct. 26, 2012 | [11 empty] | LER 4-4 Crowbar Stack SCRs removed 13+14 Sept. 2018 | [10 empty] | LER 4-4 and 2012 HVPS2 Crowbar Stack SCRs Summary
Stack 1 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? | Creeping Up? | Re-Use? |  |  |  | Stack 1 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? | Creeping Up? | Re-Use?
1 | 2510 | 8.5 | 19.6 | Good | 6.9 | Y | N | Y |  |  |  | 1 | 5311 | 7.2 | 21 | Good | 7.1 | Y | N | Y |  |  | 5311 | 7.2 | 21 | 7.1
2 | 2491 | 90.4 | 155.3 | Good | 9+ No SF | N | N | N |  |  |  | 2 | 5313 | 6.7 | 13.2 | Good | 7.1 | Y | N | Y |  |  | 5313 | 6.7 | 13.2 | 7.1
3 | 2503 | 6 | 11 | Good | 6.9 | Y | N | Y |  |  |  | 3 | 5312 | 10.4 | 25.8 | Good | 7 | Y | N | Y |  |  | 5312 | 10.4 | 25.8 | 7
4 | 2515 | 30.5 | 53.1 | Good | 6.9 | Y | N | Y |  |  |  | 4 | 5314 | 6 | 10.2 | Good | 7.1 | Y | N | Y |  |  | 5314 | 6 | 10.2 | 7.1
5 | 2511 | 14.7 | 38.8 | Good | 7 | Y | N | Y |  |  |  | 5 | 5392 | 9.5 | 31 | Good | 7 | Y | N | Y |  |  | 5392 | 9.5 | 31 | 7
6 | 2335 | 35 | 98.5 | Good | 6.9 | Y | N | Y |  |  |  | 6 | 5393 | 14.4 | 42.2 | Good | 7 | Y | N | Y |  |  | 5393 | 14.4 | 42.2 | 7
[23 empty] | 5328 | 7 | 16 | 7
[23 empty] | 5330 | 12.5 | 27.2 | 7
Stack 2 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  |  |  | Stack 2 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  |  | 5331 | 18 | 38.8 | 7.3
1 | 3503 | 24.6 | 38.2 | Good | 6.85 | Y | N | Y |  |  |  | 1 | 5328 | 7 | 16 | Good | 7 | Y | N | Y |  |  | 5329 | 46.7 | 98.5 | 7
2 | 3500 | 28.9 | 47.2 | Good | 7.1 | Y | N | Y |  |  |  | 2 | 5330 | 12.5 | 27.2 | Good | 7 | Y | N | Y |  |  | 5386 | 31.5 | 198 | 6.85
3 | 3528 | 76.8+ | 113+ | Good | 7 | Marg. | Y | N |  |  |  | 3 | 5331 | 18 | 38.8 | Good | 7.3 | Y | N | Y |  |  | 5387 | 20.3 | 84 | 6.95
4 | 3461 | 1268+ | 4000+ | Good | Short SF | N | Y | N |  |  |  | 4 | 5329 | 46.7 | 98.5 | Good | 7 | Marg. | Y | N |  |  | 5409 | 61.7 | 208.3 | 7
5 | 3523 | 87.5+ | 875+ | Good | 6.8 | Marg. | Y | N |  |  |  | 5 | 5386 | 31.5 | 198 | Good | 6.85 | Y | N | Y |  |  | 5410 | 11.4 | 20.2 | 7.1
6 | 3504 | 12.2 | 21.9 | Good | 6.8 | Y | N | Y |  |  |  | 6 | 5387 | 20.3 | 84 | Good | 6.95 | Marg. | Y | N |  |  | 5241 | 10.9 | 23.6 | 7.1
[23 empty] | 5161 | 202.5 | 334 | 7
[23 empty] | 5154 | 990 | 3100 | 7.1
[12 empty] | Stack 3 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  |  | 5244 | 43 | 163 | 7.7
[12 empty] | 1 | 5409 | 61.7 | 208.3 | Good | 7 | Marg. | N | N |  |  | 5255 | 14 | 45.6 | 7.6
Note 1: all currents listed on this sheet are in microamps (uA). | [11 empty] | 2 | 5410 | 11.4 | 20.2 | Good | 7.1 | Y | N | Y |  |  | 5407 | 19.2 | 41.8 | 7
[12 empty] | 3 | 5241 | 10.9 | 23.6 | Good | 7.1 | Y | N | Y |  |  | 5253 | 21.9 | 41.7 | 7
Note 2: "+" symbol after a leakage current number denotes creeping current. | [11 empty] | 4 | 5161 | 202.5 | 334 | Good | 7 | Marg. | Y | N |  |  | 3634 | 920 | 2700 | 7
[12 empty] | 5 | 5154 | 990 | 3100 | Good | 7.1 | N | Y | N |  |  | 5388 | 20.7 | 37 | 7
[12 empty] | 6 | 5244 | 43 | 163 | Good | 7.7 | Marg. | Y | N |  |  | 5389 | 25 | 124.5 | 7
[23 empty] | 2510 | 8.5 | 19.6
[23 empty] | 2491 | 90.4 | 155.3
[12 empty] | Stack 4 | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  |  | 2503 | 6 | 11
[12 empty] | 1 | 5255 | 14 | 45.6 | Good | 7.6 | Y | N | Y |  |  | 2515 | 30.5 | 53.1
[12 empty] | 2 | 5407 | 19.2 | 41.8 | Good | 7 | Y | N | Y |  |  | 2511 | 14.7 | 38.8
[12 empty] | 3 | 5253 | 21.9 | 41.7 | Good | 7 | Y | N | Y |  |  | 2335 | 35 | 98.5
[12 empty] | 4 | 3634 | 920 | 2700 | Good | 7 | N | N | N |  |  | 3503 | 24.6 | 38.2
[12 empty] | 5 | 5388 | 20.7 | 37 | Good | 7 | Y | N | Y |  |  | 3500 | 28.9 | 47.2
[12 empty] | 6 | 5389 | 25 | 124.5 | Good | 7 | Y | N | Y |  |  | 3528 | 76.8 | 113
[23 empty] | 3461 | 1268 | 4000
[23 empty] | 3523 | 87.5 | 875
[23 empty] | 3504 | 12.2 | 21.9
LER 4-4 Phase Stack SCRs removed 13+14 Sept. 2018 | [28 empty] | LER 4-4 Phase Tank Stacks
S1 A- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? | Creeping Up? | Re-Use? | S1 C- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? | Creeping Up? | Re-Use? |  | S2 B- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? | Creeping Up? | Re-Use?
1 | 5272 | 20.7 | 50.4 | Good | 6.9 | Y | N | Y | 1 | 5658 | 6.8 | 20 | Good | 7.6 | Y | N | Y |  | 1 | 5316 | 8.3 | 31.2 | Good | 7.1 | Y | N | Y | S1A- | 5272 | 20.7 | 50.4 | 6.9
2 | 5292 | 31 | 221.3 | Good | 6.9 | Y | N | Y | 2 | 5657 | 8.5 | 34.2 | Good | 7.5 | Y | N | Y |  | 2 | 5317 | 5.9 | 11.6 | Good | 7.3 | Y | N | Y |  | 5292 | 31 | 221.3 | 6.9
3 | 5297 | 7 | 26.1 | Good | 6.9 | Y | N | Y | 3 | 5678 | 6.1 | 19.7 | Good | 7.7 | Y | N | Y |  | 3 | 5315 | 8.4 | 17.4 | Good | 7 | Y | N | Y |  | 5297 | 7 | 26.1 | 6.9
4 | 5271 | 39 | 116 | Good | 7 | Marg. | Y | N | 4 | 5680 | 8.8 | 48.3 | Good | 7.5 | Y | N | Y |  | 4 | 5339 | 5.3 | 16.2 | Good | 7 | Y | N | Y |  | 5271 | 39 | 116 | 7
5 | 5301 | 32.8 | 208 | Good | 7 | Marg. | Y | N | 5 | 5656 | 16.2 | 67.4 | Good | 7.6 | Y | N | Y |  | 5 | 5338 | 7.9 | 16.2 | Good | 7.1 | Y | N | Y |  | 5301 | 32.8 | 208 | 7
6 | 5293 | 27.4 | 78.8 | Good | 6.85 | Marg. | N | N | 6 | 5681 | 5.5 | 11 | Good | 7.65 | Y | N | Y |  | 6 | 5337 | 6.2 | 15.7 | Good | 7.1 | Y | N | Y |  | 5293 | 27.4 | 78.8 | 6.85
[28 empty] | S1A+ | 5249 | 4.7 | 9.8 | 7
[29 empty] | 5186 | 6.4 | 14.1 | 6.9
S1 A+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? | S1 C+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | S2 B+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | 5296 | 6.8 | 17.5 | 6.9
1 | 5249 | 4.7 | 9.8 | Good | 7 | Y | N | Y | 1 | 5341 | 6.5 | 16.3 | Good | 7 | Y | N | Y |  | 1 | 5275 | 4.5 | 8.1 | Good | 7.2 | Y | N | Y |  | 5280 | 24.9 | 36.5 | 6.9
2 | 5186 | 6.4 | 14.1 | Good | 6.9 | Y | N | Y | 2 | 5273 | 89.5 | 878 | Good | 7 | Marg. | N | N |  | 2 | 5294 | 49.3 | 800 | Good | 7 | Marg. | Y | N |  | 5284 | 70 | 1048 | 6.8
3 | 5296 | 6.8 | 17.5 | Good | 6.9 | Y | N | Y | 3 | 5279 | 28.6 | 41.1 | Good | 7 | Marg. | N | N |  | 3 | 5268 | 16.1 | 31.2 | Good | 6.9 | Y | N | Y |  | 5299 | 16.9 | 36.7 | 7
4 | 5280 | 24.9 | 36.5 | Good | 6.9 | Marg. | N | N | 4 | 5340 | 7.1 | 17.6 | Good | 7.2 | Y | N | Y |  | 4 | 5267 | 21.4 | 44 | Good | 6.9 | Y | N | Y | S1B- | 5239 | 6.1 | 24.2 | 7.6
5 | 5284 | 70 | 1048 | Good | 6.8 | Marg. | Y | N | 5 | 5342 | 4.9 | 9.7 | Good | 6.95 | Y | N | Y |  | 5 | 5290 | 4.5 | 13 | Good | 6.9 | Y | N | Y |  | 5304 | 7 | 16 | 7
6 | 5299 | 16.9 | 36.7 | Good | 7 | Y | N | Y | 6 | 5343 | 4.4 | 8.8 | Good | 6.9 | Y | N | Y |  | 6 | 5298 | 13.1 | 23.3 | Good | 7.1 | Y | N | Y |  | 5269 | 25.8 | 106.5 | 6.9
[29 empty] | 5234 | 8.8 | 14.1 | 7.6
[29 empty] | 5281 | 19 | 29.2 | 6.85
S1 B- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? | S2 A- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | S2 C- | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | 5240 | 8.4 | 13.3 | 7.2
1 | 5239 | 6.1 | 24.2 | Good | 7.6 | Y | N | Y | 1 | 5385 | 10.8 | 40.6 | Good | 6.9 | Y | N | Y |  | 1 | 5307 | 11.4 | 32 | Good | 7 | Y | N | Y | S1B+ | 5239 | 6.1 | 24.2 | 7
2 | 5304 | 7 | 16 | Good | 7 | Y | N | Y | 2 | 5384 | 9.5 | 46.2 | Good | 6.9 | Y | N | Y |  | 2 | 5308 | 10 | 19.4 | Good | 7 | Y | N | Y |  | 5304 | 7 | 16 | 7.65
3 | 5269 | 25.8 | 106.5 | Good | 6.9 | Y | N | Y | 3 | 5383 | 8.8 | 30 | Good | 6.9 | Y | N | Y |  | 3 | 5309 | 11.4 | 31.2 | Good | 7.1 | Y | N | Y |  | 5269 | 25.8 | 106.5 | 7
4 | 5234 | 8.8 | 14.1 | Good | 7.6 | Y | N | Y | 4 | 5382 | 4.9 | 9.8 | Good | 7 | Y | N | Y |  | 4 | 5310 | 18 | 32.2 | Good | 7.2 | Y | N | Y |  | 5234 | 8.8 | 14.1 | 7
5 | 5281 | 19 | 29.2 | Good | 6.85 | Y | N | Y | 5 | 5336 | 6.4 | 20.3 | Good | 7.3 | Y | N | Y |  | 5 | 5667 | 11 | 34.8 | Good | 7 | Y | N | Y |  | 5281 | 19 | 29.2 | 6.8
6 | 5240 | 8.4 | 13.3 | Good | 7.2 | Y | N | Y | 6 | 5659 | 5.1 | 11 | Good | 7.6 | Marg | N | N |  | 6 | 5668 | 5 | 9.7 | Good | 7.5 | Y | N | Y |  | 5240 | 8.4 | 13.3 | 7
[28 empty] | S1C- | 5658 | 6.8 | 20 | 7.6
[29 empty] | 5657 | 8.5 | 34.2 | 7.5
S1 B+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? | S2 A+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | S2 C+ | S/N | I @ 4.2 KV | I @ 6.5 KV | F.O. | S. F. KV | Pass? |  | Re-Use? |  | 5678 | 6.1 | 19.7 | 7.7
1 | 5289 | 5 | 10.6 | Good | 7 | Y | N | Y | 1 | 5424 | 7.2 | 18.1 | Good | 7 | Y | N | Y |  | 1 | 5238 | 4 | 9.6 | Good | 7 | Y | N | Y |  | 5680 | 8.8 | 48.3 | 7.5
2 | 5236 | 5.6 | 11 | Good | 7.65 | Y | N | Y | 2 | 5424 | 8.8 | 17.2 | Good | 7.4 | Y | N | Y |  | 2 | 5266 | 6.6 | 13.3 | Good | 7.1 | Y | N | Y |  | 5656 | 16.2 | 67.4 | 7.6
3 | 5306 | 132.2 | 2000 | Good | 7 | Marg. | N | N | 3 | 5425 | 13.5 | 41.7 | Good | 7.35 | Y | N | Y |  | 3 | 5295 | 31.7 | 98 | Good | 7 | Y | N | Y |  | 5681 | 5.5 | 11 | 7.65
4 | 5274 | 10.2 | 20 | Good | 7 | Y | N | Y | 4 | 5426 | 18.8 | 49 | Good | 7.2 | Y | N | Y |  | 4 | 5288 | 20 | 145 | Good | 7.6 | Y | N | Y | S1C+ | 5341 | 6.5 | 16.3 | 7
5 | 5278 | 14.3 | 21.8 | Good | 6.8 | Marg. | N | N | 5 | 5264 | 112.2 | 978 | Good | 7 | Marg. | N | N |  | 5 | 5258 | 13.9 | 47.5 | Good | 7.1 | Y | N | Y |  | 5273 | 89.5 | 878 | 7
6 | 5303 | 9.9 | 24.3 | Good | 7 | Y | N | Y | 6 | 5270 | 6.2 | 16.7 | Good | 7 | Y | N | Y |  | 6 | 5283 | 6.3 | 13.3 | Good | 6.85 | Y | N | Y |  | 5279 | 28.6 | 41.1 | 7
[29 empty] | 5340 | 7.1 | 17.6 | 7.2
[29 empty] | 5342 | 4.9 | 9.7 | 6.95
[29 empty] | 5343 | 4.4 | 8.8 | 6.9
[28 empty] | S2A- | 5385 | 10.8 | 40.6 | 6.9
[29 empty] | 5384 | 9.5 | 46.2 | 6.9
[29 empty] | 5383 | 8.8 | 30 | 6.9
[29 empty] | 5382 | 4.9 | 9.8 | 7
[29 empty] | 5336 | 6.4 | 20.3 | 7.3
[29 empty] | 5659 | 5.1 | 11 | 7.6
[28 empty] | S2A+ | 5424 | 7.2 | 18.1 | 7
[29 empty] | 5424 | 8.8 | 17.2 | 7.4
[29 empty] | 5425 | 13.5 | 41.7 | 7.35
[29 empty] | 5426 | 18.8 | 49 | 7.2
[29 empty] | 5264 | 112.2 | 978 | 7
[29 empty] | 5270 | 6.2 | 16.7 | 7
[28 empty] | S2B- | 5316 | 8.3 | 31.2 | 7.1
[29 empty] | 5317 | 5.9 | 11.6 | 7.3
[29 empty] | 5315 | 8.4 | 17.4 | 7
[29 empty] | 5339 | 5.3 | 16.2 | 7
[29 empty] | 5338 | 7.9 | 16.2 | 7.1
[29 empty] | 5337 | 6.2 | 15.7 | 7.1
[28 empty] | S2B+ | 5275 | 4.5 | 8.1 | 7.2
[29 empty] | 5294 | 49.3 | 800 | 7
[29 empty] | 5268 | 16.1 | 31.2 | 6.9
[29 empty] | 5267 | 21.4 | 44 | 6.9
[29 empty] | 5290 | 4.5 | 13 | 6.9
[29 empty] | 5298 | 13.1 | 23.3 | 7.1
[28 empty] | S2C- | 5307 | 11.4 | 32 | 7
[29 empty] | 5308 | 10 | 19.4 | 7
[29 empty] | 5309 | 11.4 | 31.2 | 7.1
[29 empty] | 5310 | 18 | 32.2 | 7.2
[29 empty] | 5667 | 11 | 34.8 | 7
[29 empty] | 5668 | 5 | 9.7 | 7.5
[28 empty] | S2C+ | 5238 | 4 | 9.6 | 7
[29 empty] | 5266 | 6.6 | 13.3 | 7.1
[29 empty] | 5295 | 31.7 | 98 | 7
[29 empty] | 5288 | 20 | 145 | 7.6
[29 empty] | 5258 | 13.9 | 47.5 | 7.1
[29 empty] | 5283 | 6.3 | 13.3 | 6.85
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## spare stacks
New Spare Crowbar Stacks for Spear 1+2.
SCRs are from LER 4-4 which were removed 14 Sept. 2018
|  |  | Set 1 | Date: Oct 2, 2018 | [5 empty] | Set 2 | Date: Oct 6, 2018
| Stack 1 | SCR S/N | Stack Leakage @ 25 KVDC | Fiber Optic Trig Test | SF KV | Pass/Fail | uA @ 4.2 kV | Stack 1 | SCR S/N | Stack Leakage @ 25 KVDC | Fiber Optic Trig Test | SF KV | Pass/Fail | uA @ 4.2 kV
| Cell 1 | 5389 |  |  |  |  | 25 | Cell 1 | 5289 |  |  |  |  | 5
| Cell 2 | 5281 |  |  |  |  | 19 | Cell 2 | 5270 |  |  |  |  | 6.2
| Cell 3 | 5311 | .850 mA | Good | 40.56 | Pass | 7.2 | Cell 3 | 5424 | .841 mA | Good | 40.05 | Pass | 7.2
| Cell 4 | 2335 |  |  |  |  | 35 | Cell 4 | 5336 |  |  |  |  | 6.4
| Cell 5 | 5240 |  |  |  |  | 8.4 | Cell 5 | 5385 |  |  |  |  | 10.8
| Cell 6 | 5304 |  |  |  |  | 7 | Cell 6 | 5383 |  |  |  |  | 8.8
| Stack 2 | [6 empty] | Stack 2
| Cell 1 | 5307 |  |  |  |  | 11.4 | Cell 1 | 5343 |  |  |  |  | 4.4
| Cell 2 | 5393 |  |  |  |  | 14.4 | Cell 2 | 5186 |  |  |  |  | 6.4
| Cell 3 | 5288 | .855 mA | Good | 41.07 | Pass | 20 | Cell 3 | 5317 | .836 mA | Good | 40.04 | Pass | 5.9
| Cell 4 | 2503 |  |  |  |  | 6 | Cell 4 | 5303 |  |  |  |  | 9.9
| Cell 5 | 2511 |  |  |  |  | 14.7 | Cell 5 | 5337 |  |  |  |  | 6.2
| Cell 6 | 5309 |  |  |  |  | 11.4 | Cell 6 | 5382 |  |  |  |  | 4.9
| Stack 3 | [6 empty] | Stack 3
| Cell 1 | 5283 |  |  |  |  | 6.3 | Cell 1 | 5290 |  |  |  |  | 4.5
| Cell 2 | 5330 |  |  |  |  | 12.5 | Cell 2 | 5297 |  |  |  |  | 7
| Cell 3 | 5295 | .857 mA | Good | 41.08 | Pass | 31.7 | Cell 3 | 5423 | .837 mA | Good | 40 | Pass | ?
| Cell 4 | 5238 |  |  |  |  | 4 | Cell 4 | 5384 |  |  |  |  | 9.5
| Cell 5 | 5269 |  |  |  |  | 25.8 | Cell 5 | 5236 |  |  |  |  | 5.6
| Cell 6 | 5255 |  |  |  |  | 14 | Cell 6 | 5249 |  |  |  |  | 4.7
| Stack 4 | [6 empty] | Stack 4
| Cell 1 | 5314 |  |  |  |  | 6 | Cell 1 | 5339 |  |  |  |  | 5.3
| Cell 2 | 5392 |  |  |  |  | 9.5 | Cell 2 | 5296 |  |  |  |  | 6.8
| Cell 3 | 5331 | .856 mA | Good | 41.21 | Pass | 18 | Cell 3 | 5341 | .836 mA | Good | 40.34 | Pass | 6.5
| Cell 4 | 5407 |  |  |  |  | 19.2 | Cell 4 | 5340 |  |  |  |  | 7.1
| Cell 5 | 2510 |  |  |  |  | 8.5 | Cell 5 | 5275 |  |  |  |  | 4.5
| Cell 6 | 5239 |  |  |  |  | 6.1 | Cell 6 | 5342 |  |  |  |  | 4.9

## HVPS1 stacks 20190226
|  |  |  | Cold Tests @ 22 deg. C | [8 empty] | Hot Tests @ approx. 50 deg. C |  |  |  | HVPS1 Stack Summary
[17 empty] | Cold Tests |  | Hot Tests
Stack 1 | SCR # | Serial # | Date Code | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Re-Use? | Stack 1 | SCR # | Serial # | Date Code | uA @ 4.2 KV | uA @ 6.5KV | AnodeTemp | Serial No. | 4.2 kV | 6.5 kV | 4.2 kV | 6.5 kV
| 1 | 3506 | 20S4 | 20.8 | 33.94 | G | 7.32 | Y |  | 1 | 3506 | 20S4 | 133.7+ | 226.5+ | 50.35 | 3506 | 20.8 | 33.94 | 133.7 | 226.5
| 2 | 3006 | 02S4 | 13.6 | 26.2 | G | 7.24 | Y |  | 2 | 3006 | 02S4 | 220.5+ | 375+ | 50.75 | 3006 | 13.6 | 26.2 | 220.5 | 375
| 3 | 3205 | 02S4 | 34 | 65 | G | 7.2 | Y |  | 3 | 3205 | 02S4 | 319+ | 586+ | 51.25 | 3205 | 34 | 65 | 319 | 586
| 4 | 3290 | 25S5 | 28.4 | 68.4 | G | 7.4 | Y |  | 4 | 3290 | 25S5 | 146.5+ | 322.2+ | 51.3 | 3290 | 28.4 | 68.4 | 146.5 | 322.2
| 5 | 3170 | 02S4 | 3.1 | 5.1 | G | 7.12 | Y |  | 5 | 3170 | 02S4 | 52.1+ | 101.1+ | 51.8 | 3170 | 3.1 | 5.1 | 52.1 | 101.1
| 6 | 3209 | 02S4 | 38.1 | 73.3 | G | 7.84 | Y |  | 6 | 3209 | 02S4 | 344+ | 609+ | 50.55 | 3209 | 38.1 | 73.3 | 344 | 609
[16 empty] | 2502 | 13.6 | 27.9 | 91.2 | 182.6
Stack 2 | SCR # | Serial # | Date Code | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Re-Use? | Stack 2 | SCR # | Serial # |  |  |  |  | 3507 | 24.7 | 41 | 122.2 | 273.6
| 1 | 2502 | 24R3 | 13.6 | 27.9 | G | 7.1 | Y |  | 1 | 2502 | 24R3 | 91.2+ | 182.6+ | 51.5 | 3187 | 12.3 | 23.3 | 153.6 | 287.9
| 2 | 3507 | 25S5 | 24.7 | 41 | G | 7.2 | Y |  | 2 | 3507 | 25S5 | 122.2+ | 273.6+ | 50.55 | 2509 | 5.8 | 10.5 | 58.8 | 115.2
| 3 | 3187 | 02S4 | 12.3 | 23.3 | G | 8.2 | Y |  | 3 | 3187 | 02S4 | 153.6+ | 287.9+ | 50.75 | 2492 | 42.1 | 84.2 | 205.5 | 395.2
| 4 | 2509 | 24R3 | 5.8 | 10.5 | G | 7.1 | Y |  | 4 | 2509 | 24R3 | 58.8+ | 115.2+ | 50.05 | 2508 | 5.2 | 10.8 | 105.1 | 440.6
| 5 | 2492 | 24R3 | 42.1 | 84.2 | G | 8.1 | Y |  | 5 | 2492 | 24R3 | 205.5+ | 395.2+ | 51.5 | 5718 | 25.1 | 138.5 | 63.9 | 128.4
| 6 | 2508 | 24R3 | 5.2 | 10.8 | G | 7 | Y |  | 6 | 2508 | 24R3 | 105.1+ | 440.6+ | 50.05 | 2351 | 6.5 | 11.8 | 551 | 1015
[16 empty] | 5685 | 162 | 219 | 641 | 1104
Stack 3 | SCR # | Serial # | Date Code | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Re-Use? | Stack 3 | SCR # | Serial # |  |  |  |  | 5637 | 36 | 104 | 259.1 | 548
| 1 | 5718 | 06U2 | 25.1 | 138.5 | G | 7.2 | Y |  | 1 | 5718 | 06U2 | 63.9+ | 128.4+ | 50.3 | 5670 | 65 | 1500 | 10000 | 10000
| 2 | 2351 | 08U2 | 6.5 | 11.8 | G | 8.24 | Y |  | 2 | 2351 | 08U2 | 551+ | 1015+ | 50.25 | 5650 | 5.1 | 9.2 | 45.5 | 10000
| 3 | 5685 | 18R2 | 162+ | 219+ | G | 6.92 | N |  | 3 | 5685 | 18R2 | 641+ | 1104+ | 50.3 | 3015 | 86 | 153 | 464.4 | 895
| 4 | 5637 | 06U2 | 36 | 104 | G | 7.64 | Y |  | 4 | 5637 | 06U2 | 259.1+ | 548+ | 49.95 | 3230 | 16 | 40 | 218.1 | 371.2
| 5 | 5670 | 06U2 | 65+ | Shorted | G | 7.6 | N |  | 5 | 5670 | 06U2 | N/A | N/A |  | 3233 | 192 | 1402 | 985 | 1985
| 6 | 5650 | 06U2 | 5.1 | 9.2 | G | 7.68 | Y |  | 6 | 5650 | 06U2 | 45.5+ | Shorted | 50.45 | 3203 | 68 | 115 | 359.5 | 757
[16 empty] | 3204 | 70 | 108 | 607 | 1139
Stack 4 | SCR # | Serial # | Date Code | uA @ 4.2 KV | uA @ 6.5KV | F.O. Trigs | OV Self-Fire | Re-Use? | Stack 4 | SCR # | Serial # |  |  |  |  | 3232 | 51.4 | 117 | 280.5 | 651
| 1 | 3015 | 02S4 | 86 | 153 | G | 7.12 | Y |  | 1 | 3015 | 02S4 | 464.4+ | 895+ | 50.25
| 2 | 3230 | 02S4 | 16 | 40 | G | 7.08 | Y |  | 2 | 3230 | 02S4 | 218.1+ | 371.2+ | 50.6
| 3 | 3233 | 02S4 | 192+ | 1402+ | G | 7.12 | N |  | 3 | 3233 | 02S4 | 985+ | 1985+ | 50.2
| 4 | 3203 | 02S4 | 68 | 115 | G | 7.08 | Y |  | 4 | 3203 | 02S4 | 359.5+ | 757+ | 50.5
| 5 | 3204 | 02S4 | 70 | 108 | G | 7 | Y |  | 5 | 3204 | 02S4 | 607+ | 1139+ | 51.3
| 6 | 3232 | 02S4 | 51.4 | 117 | G | 7.2 | Y |  | 6 | 3232 | 02S4 | 280.5+ | 651+ | 50.6
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## spare crowbar stacks 20190327
New Spare Stacks Made From Spear 1 Crowbar Stack SCRs.
2019-03-27
| Stack 1 | SCR S/N | Date Code | Stack Leakage @ 25 KVDC | Fiber Optic Trig Test | Pass/Fail | uA @ 4.2 kV
| Cell 1 | 3506 | 20S4 |  |  |  | 20.8
| Cell 2 | 3006 | 02S4 |  |  |  | 13.6
| Cell 3 | 3205 | 02S4 |  |  |  | 34
| Cell 4 | 3290 | 25S5 | .834 mA | Good | Pass | 28.4
| Cell 5 | 3170 | 02S4 |  |  |  | 3.1
| Cell 6 | 3209 | 02S4 |  |  |  | 38.1
Stack 2
| Cell 1 | 2502 | 24R3 |  |  |  | 13.6
| Cell 2 | 3507 | 25S5 |  |  |  | 24.7
| Cell 3 | 3187 | 02S4 |  |  |  | 12.3
| Cell 4 | 2509 | 24R3 | .831 mA | Good | Pass | 5.8
| Cell 5 | 2492 | 24R3 |  |  |  | 42.1
| Cell 6 | 2508 | 24R3 |  |  |  | 5.2
Stack 3
| Cell 1 | 5718 | 08U2 |  |  |  | 25.1
| Cell 2 | 2351 | 18R2 |  |  |  | 6.5
| Cell 3 | 5685 | 06U2 |  |  |  | 162
| Cell 4 | 5637 | 06U2 | .851 mA | Good | Pass | 36 | Replaced S/N | Date Code
| Cell 5 | 5640 | 06U2 |  |  |  | 11.6 | 5670 | 06U2
| Cell 6 | 3184 | 02S4 |  |  |  | ? | 5650 | 06u2
Stack 4
| Cell 1 | 6287 | 20U9 |  |  |  | 13.2 | 3015 | 02S4
| Cell 2 | 3230 | 02S4 |  |  |  | 16
| Cell 3 | 6224 | 20U9 |  |  |  | 13.8 | 3233 | 02S4
| Cell 4 | 3203 | 02S4 | .849 mA | Good | Pass | 68
| Cell 5 | 3204 | 02S4 |  |  |  | 70
| Cell 6 | 3232 | 02S4 |  |  |  | 51.4
All 4 stacks good and ready for spares use.