## HVPS2
2020-07-31 | S2 C+ | [5 empty] | 2020-08-18 | S2 C- |  | bare SCR | [6 empty] | dressed SCR
V_total (kV) | 24.91 | SCR (1=top) | V_top (kV) | V_bot (kV) | V_del (kV) | R (Mohm) | V_total (kV) | 25.145 | SCR (1=top) | V_top (V) | V_bot (V) | V_del (kV) | R (Mohm) | V_total (kV) | 25.298 | SCR (1=top) | V_top (V) | V_bot (V) | V_del (kV) | R (Mohm)
I (uA) | 136.51 | 1 | 24.91 | 22.82 | 2.09 | 15.3102 | I (uA) | 22.6 | 1 | 0 | 1899 | 1.899 | 84.0265 | I (uA) | 92.9 | 1 | 0 | 1958 | 1.958 | 21.0764
R (Mohm) | 182.4775 | 2 | 22.82 | 20.87 | 1.95 | 14.2847 | R (Mohm) | 1112.6106 | 2 | 1899 | 3471 | 1.572 | 69.5575 | R (Mohm) | 272.3143 | 2 | 1958 | 3819 | 1.861 | 20.0323
|  | 3 | 20.87 | 18.83 | 2.04 | 14.944 |  |  | 3 | 3471 | 5387 | 1.916 | 84.7788 |  |  | 3 | 3819 | 5634 | 1.815 | 19.5371
|  | 4 | 18.83 | 16.9 | 1.93 | 14.1382 |  |  | 4 | 5387 | 6465 | 1.078 | 47.6991 |  |  | 4 | 5634 | 7557 | 1.923 | 20.6997
|  | 5 | 16.9 | 14.95 | 1.95 | 14.2847 |  |  | 5 | 6465 | 8470 | 2.005 | 88.7168 |  |  | 5 | 7557 | 9452 | 1.895 | 20.3983
|  | 6 | 14.95 | 12.96 | 1.99 | 14.5777 |  |  | 6 | 8470 | 10597 | 2.127 | 94.115 |  |  | 6 | 9452 | 11432 | 1.98 | 21.3132
|  | 7 | 12.96 | 11.12 | 1.84 | 13.4789 |  |  | 7 | 10597 | 12713 | 2.116 | 93.6283 |  |  | 7 | 11432 | 13328 | 1.896 | 20.409
|  | 8 | 11.12 | 9.12 | 2 | 14.6509 |  |  | 8 | 12713 | 14566 | 1.853 | 81.9912 |  |  | 8 | 13328 | 15136 | 1.808 | 19.4618
|  | 9 | 9.12 | 7.13 | 1.99 | 14.5777 |  |  | 9 | 14566 | 16503 | 1.937 | 85.708 |  |  | 9 | 15136 | 16861 | 1.725 | 18.5684
|  | 10 | 7.13 | 5.199 | 1.931 | 14.1455 |  |  | 10 | 16503 | 18687 | 2.184 | 96.6372 |  |  | 10 | 16861 | 18854 | 1.993 | 21.4532
|  | 11 | 5.199 | 3.253 | 1.946 | 14.2554 |  |  | 11 | 18687 | 20419 | 1.732 | 76.6372 |  |  | 11 | 18854 | 20522 | 1.668 | 17.9548
|  | 12 | 3.253 | 1.273 | 1.98 | 14.5044 |  |  | 12 | 20419 | 22136 | 1.717 | 75.9735 |  |  | 12 | 20522 | 22252 | 1.73 | 18.6222
|  | 13 | 1.273 | 0 | 1.273 | 9.3253 |  |  | 13 | 22136 | 23576 | 1.44 | 63.7168 |  |  | 13 | 22252 | 23709 | 1.457 | 15.6835
[9 empty] | 14 | 23576 | 25145 | 1.569 | 69.4248 |  |  | 14 | 23709 | 25298 | 1.589 | 17.1044
|  |  |  | average | 1.9162 | 14.0367
|  |  |  | std | 0.19427 | 1.4231 |  |  |  |  | average | 1.7961 | 79.4722 |  |  |  |  | average | 1.807 | 19.451
[11 empty] | std | 0.29382 | 13.0009 |  |  |  |  | std | 0.15152 | 1.631
|  |  |  | avg (good) | 1.9698 | 14.4293
|  |  |  | std (good) | 0.059509 | 0.43593
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.