# Technical Note: Ross Engineering Primary Energy Storage
LLRF/MODE System Schematic

Source Document: DOC041421-04142021114320.pdf / rossEngr713203.pdf (identical drawings)
Document Type: Technical Note – Circuit Schematic Analysis
Purpose: Detailed extraction of design information from circuit schematic for AI-assisted design reconstruction

────────────────────────────────────────────────────────────

# 1. Document Identification

## 1.1 Title Block Information

Title: PRIMARY ENERGY STORAGE LLRF/MODE SYSTEM SCHEMATIC

Drawing Number: 713203

Company: Ross Engineering Corp.

Address: 590 Westchester Dr., Campbell, CA 95008

Part/Model Number: P/N B20360

Associated Panel: HCA-1-A (HVPS Control Assembly)

Date Received: APR 14, 2021

Received By: AZ (initials)

File Reference: Vault CFTATOR / BT BIOS

## 1.2 Revision History (Corrections and Additions Block)

Rev A: Initial release (date: 3/5 approx.)

Rev B: Customer Change (date: 1/5 approx.)

Rev C: Added terminal numbers, equipment ratings (date: unknown)

Rev D: See ECN #3110, dated 2/2-83 (Engineering Change Notice)

# 2. Circuit Overview

This schematic depicts a High-Voltage (HV) Energy Storage system used for closing a vacuum contactor. The circuit is designed by Ross Engineering Corp. and is a primary energy storage system for an LLRF/MODE (Low-Level RF/Mode) application. The system stores energy in capacitors and releases it to close a high-voltage vacuum contactor used in switchgear. The design includes control circuitry for open/close operations, safety interlocks, voltage sensing, and operational status indication.

# 3. Power Supply Section

## 3.1 AC Input

AC Input Voltage: 115 VAC (from line)

The AC input feeds the control power transformer and energy storage rectifier

HV AC connection present for main vacuum contactor line contacts

## 3.2 DC Energy Storage

Energy storage capacitors charged to approximately 300-800 VDC

Discharge time to 80V is approximately 5 minutes (if not automatic)

Discharge time to 40V is approximately 10 minutes (if not automatic)

The DC holding coil operates from stored DC energy

Voltage sensor monitors capacitor charge level

Voltage sensor location: connected to +350 VDC rail

## 3.3 Transformer

Control transformer: 35-180 VA rating

Output: 120V secondary

Powers control circuitry and charging circuit

# 4. Component List

## 4.1 Relays and Contactors

MX - Remote Close Relay (main close command relay)

K1 - Main operating relay

K2 - Ready relay (indicates energy storage ready for closing)

K3 - Current sensing relay (monitors holding coil current)

R2 - Relay (Allen Bradley Size 1 contactor)

R3 - Relay

CR1 - Control relay

CR2 - Control relay

BR - Blocking relay

TX - Local tripping relay / Aux tripping relay

## 4.2 Indicators and Counters

READY IND. - Ready indicator (local)

NOT READY IND. - Not ready indicator

OPEN IND. - Open indicator light

CLOSE IND. - Close indicator

OPERATIONS COUNTER - Counts close operations (600V rated)

MED COUNTER - Operations counter (metered)

## 4.3 Protection Components

Fuses: 6 AMP, 800V rated

Voltage Sensor: Connected to +350 VDC bus

OT-100 (5A) - Overcurrent protection device

INTLK - Interlock (25A rated)

Door interlocks on energy storage driver

Remote safety discharge interlocks

## 4.4 Coils and Solenoids

HOLDING COIL (L1) - DC holding and dropout coil for vacuum contactor

CLOSE COIL (L2) - Energy storage closing coil

FAM - 8/ip AMP rated

SLD BLO - Solenoid block

## 4.5 Motor/Drive Components

Allen Bradley Size 1 contactor (R2 associated)

Motor rated at 120V, 1/2 or 3 AMPS

Operating at 300 VDC to 800+ VDC

# 5. Circuit Topology and Connections

## 5.1 Main Power Path

AC line input → Line contacts (HV VAC) → Load

The vacuum contactor controls the main HV power path

Line contacts are NO (Normally Open) type

## 5.2 Control Circuit

MX relay (remote close command) initiates closing sequence

Current sensing relay K3 verifies holding coil current

When K3 confirms current, and K2 (ready) is closed, K1 energizes

K1 applies stored energy from capacitors to closing coil L2

L2 solenoid closes toggle mechanism which closes HV contacts

Holding coil L1 maintains contactor in closed position

## 5.3 Energy Storage and Charging

AC power is rectified and charges energy storage capacitors

Voltage sensor monitors charge level on +350 VDC bus

When capacitors reach sufficient voltage, K2 (ready relay) closes

Ready indicator illuminates to show system is ready to close

## 5.4 Opening Sequence

MX opened (or TX local off, or interlocks open) starts opening

DC current to L1 holding coil is interrupted

L1 drops out within 1 cycle, dropping toggle base

HV vacuum contactor opens and clears in ~1/2 to 1 cycle

Toggle breaks and resets L1 and L2 for reclosing

# 6. Safety and Interlock Systems

## 6.1 Door Interlocks

Safety door interlocks (S1, S2) shown with door closed position

Both energy storage capacitors discharge within 5 seconds when door is opened

Door interlock on energy storage driver unit automatically discharges capacitors

## 6.2 Remote Safety

Remote safety circuit provides external discharge path

Vacuum discharge interlocks present

Cap dump circuit available for manual capacitor discharge

## 6.3 Blocking Relay (BR)

If BR blocking relay closed by excessive fault, MX and TX local off are bypassed

Contactor cannot open immediately if AC is lost while BR stays closed

With loss of AC control voltage, contactor holds for at least 170 milliseconds

# 7. Terminal and Connector Details

## 7.1 Identified Terminals

LOAD terminals for external connection

LINE 1 input terminal

HV AC connections

Control voltage terminals (115 VAC, 120V)

DC bus terminals (+350 VDC)

## 7.2 Interconnection Notes

Suggested interconnections by user for field wiring

Temperature sensor (TEMP) connection point

Door lock connections (RO-R13)

Cap dump connections

Remote safety connections

# 8. Design Notes and Cautions

CAUTION: This is a HV energy storage device operating at 300 to 800+ VDC

Discharge time to 80V is approximately 5 minutes

Discharge time to 40V is approximately 10 minutes if not automatic

Before touching live parts, remove power and wait at least 5 minutes, then short both capacitors

Close circuits should be wired with at least #14 wire

If there is considerable distance between breaker, energy storage supply, or close relay, at least #12 wire should be used

115 VAC power requirement is 1/2 AMP continuous

Safety door interlocks S1 and S2 shown with door closed; both energy storage capacitors are discharged within 5 seconds when door is opened

Contactor should be de-energized in normal (default) position

Remote safety: closed = driver door closed and de-energized

# 9. Operating Principles Summary

This circuit is a high-voltage energy storage closing system for a vacuum contactor. The system charges capacitors to approximately 350 VDC through a rectifier powered by the control transformer. When a close command is received (via MX relay), the system verifies that energy storage is adequate (via K2 ready relay) and that holding coil current is present (via K3 current sensing relay). Upon verification, stored energy is applied to the closing coil (L2), which mechanically closes the vacuum contactor's HV contacts through a toggle mechanism. The holding coil (L1) then maintains the contactor in the closed state using DC power. To open, the holding coil current is interrupted, causing the toggle to release and open the HV contacts within ~1 cycle. Multiple safety interlocks prevent unauthorized operation, and door interlocks automatically discharge the capacitors when the cabinet is opened. The blocking relay (BR) provides fault ride-through capability by preventing premature opening during excessive fault conditions.