# Technical Note: 12.47 KV Outdoor Metal Enclosed
Combination Vacuum Contactor Controller
Schematic Diagram & General Arrangement

Source Document: gp3085000103.pdf
Document Type: Technical Note – Circuit Schematic Analysis
Purpose: Detailed extraction of design information from circuit schematic for AI-assisted design reconstruction

────────────────────────────────────────────────────────────

# 1. Document Identification

## 1.1 Title Block Information

Title: 12.47 KV OUTDOOR METAL ENCL. COMB. VAC. CONTACTOR CONTROLLER

Subtitle: SCHEMATIC DIAG. & GEN ARRG'MT (Schematic Diagram & General Arrangement)

Drawing Number: GP-308-500-01-R3

Prefix: GP, Base: 308, Suffix: 500-01, Revision: R3

Organization: Lawrence Berkeley Laboratory (LBL)

Project: Positron-Electron Project (PEP / PEP-II at SLAC)

Drawn by: C. Johnson

Checked by: L. Johnson

Scale: Not to scale (general arrangement); dimensions in millimeters unless otherwise specified

SLAC Release reference: V:\MDCAD\DocumentControl\images\Incoming\SLAC\PEP2 VCC1.dgn.tif

Release date: 9/25/2006 12:04:54 PM

## 1.2 Revision History

Rev A1: Changed capacitor connections in DC power supply, added terminal for HV time meter, identified VAC contactor aux contacts, located circuit breaker, revised VAC contactor internal wiring to suit

Rev A2: Changed location of bus throat connection cut-out, current transformers, ammeters, added Detail 1, relays 27, MX, IR & RR

Rev A3: Revised physical dimensions for switchgear/vacuum contactor, door-in-door arrangement (W/P)

# 2. Circuit Overview

This is a comprehensive schematic diagram and general arrangement drawing for a 12.47 kV outdoor metal-enclosed combination vacuum contactor controller system. It is part of the PEP-II (Positron-Electron Project II) at SLAC (Stanford Linear Accelerator Center) / Lawrence Berkeley Laboratory. The drawing covers the complete switchgear system including the vacuum contactor, variable voltage transformer, HV power supply, protection relays, current transformers, and the physical arrangement of all equipment within the metal enclosure. The system feeds RF power supplies via a loop feed configuration at 12.47 kV.

# 3. System Architecture

## 3.1 Power Distribution

Input: 12.47 KV feeder for loop feed

Cable: 3/C 350MCM EPR 220MILS insulation from area substation

Feed configuration: Loop feed to next vacuum contactor controller

Incoming feed: 3/C 350MCM underground conduit area

Output feeds: To variable voltage transformer (VVT) and HV power supply (HVPS)

## 3.2 Major Equipment Sections (Physical Arrangement)

Vacuum Contactor Compartment: Houses the 15kV 400A 3-pole vacuum contactor with heater

Controller Section: Contains switchgear control circuitry

Combination Power Section: Variable voltage rectifier transformer and power supply

Bus Throat Connection: 4"C existing bus throat with throat flange (see Detail 1)

Conduit to Building: Through building wall (by others)

## 3.3 Enclosure Specifications

NEMAT enclosure rated: 48" × 140" MAX overall dimensions

Configuration: Door-in-door arrangement (W/P = weatherproof)

Base plan: Concrete pad 7' × 15'/A\

Viewing window: Located on front panel with high voltage switch

Gravity close mechanism on top section

Vent: 43" with 45° opening cover (72" × 42")

Wipe cover: 12" width, full-length BLE panels, removable

Stress cone area adjacent to surge arrestor

# 4. Switchgear Control Schematic

## 4.1 Protection Relays

27 - Under Voltage Relay

MX - Remote Control Relay, 24VDC

IP - Interposing Relay, 24VDC

RR - Remote Reset Relay, 24VDC

50-51 - Over Current Relay: 2-6A with 20-40A instantaneous attachment, Type CO-6 or equal

50-51N - Grounding Over Current Relay: 0.5-2.5A with 20-40A instantaneous attachment, Type CO-6 or equal

TX - Aux Tripping Relay

BR - Blocking Relay

M - Main Operating and Holding Coils

## 4.2 Current Transformers

CT ratio: 50/5 (on each phase A, B, C)

Multiple sets of CTs for phase and neutral current measurement

CT connections to 50-51A, 50-51B, 50-51C, and 50-51N relays

## 4.3 Control Circuit Details

Control voltage source: 120VAC at RF panel (see panel schedule)

Local control switch: Trip function (OL = local control switch-trip)

Blocking relay (BR): Activated when fault current exceeds 2000 AMPS

UZ - Blocking relay function

Event counter for trip operations

## 4.4 Vacuum Contactor

Rating: 15kV, 400A, 3-pole

Type: HQ3 model (Ross Engineering)

Heater: Typical installation on each compartment

Surge arrester: Installed on incoming line side

Operating mechanism: Stored energy closing with toggle mechanism

# 5. Terminal Block Assignments

## 5.1 TB1 (Main Terminal Block)

TB1 terminals shown with numbered connections (1-20+)

Carries control circuit wiring between switchgear sections

## 5.2 TB2 (Vacuum Contactor Terminal Block)

TB2-1 through TB2-20+: Connections to vacuum contactor driver

Includes connections for reset, VAC contactor, VVT, and HVPS

## 5.3 External Connections

Input connections: L1, L2 (power), X1, X2, X3, X8 (control/aux)

Current transformer secondaries: Connected to relay panel

Cabinet/panel wiring: O/TEMP sensor, MX, BR relay connections

Flexible bus by subcontractor (furnished by others)

Installation by subcontractor for bus throat connections

# 6. Reference Drawings

GP-308-500-03: Vacuum contactor control schematic and operation instruction

ID-308-515-83: External wiring connections / connection diagram / layout

ID-308-515-91: Block diagram

ID-308-515-96: VVT & HVPS schematic diagram

Ross Engineering DWG #713203: Vacuum contactor/driver circuitry

# 7. Physical Arrangement Notes

## 7.1 Front Elevation

Viewing window on upper section

High voltage switch accessible from front

Surge arrestor location

Bus throat connection (see Detail 1)

Circuit breaker access

## 7.2 Side Elevation (Internal)

Vacuum contactor compartment

Fuse access panel

Ground connection for protective barrier

Provide gasket at rear barrier

Over VAC contactor protective barrier

Heater location below contactor

## 7.3 Rear Elevation

Access to rear compartment

Incoming 3/C 350MCM conduit area (underground)

Loop feed configuration

## 7.4 Detail 1 - Throat Flange

Bus throat connection detail (not to scale)

Shows existing 4"C bus throat interface

Flange mounting details for connection to building bus

Receptacle: S/A receptacle with 32" bolt holes and 1/2" bolts

# 8. Legend and Symbols

27: Under voltage relay

MX: Remote control relay - 24VDC

IP: Interposing relay - 24VDC

RR: Remote reset relay - 24VDC

50-51: Over current relay 2-6A with 20-40A instantaneous attachment, Type CO-6 or equal

50-51N: Grounding over current relay 0.5-2.5A with 20-40A instantaneous, Type CO-6 or equal

OL: Local control switch - trip

TX: Aux tripping relay

BR: Blocking relay

M: Main operating and holding coils

# 9. Operating Principles Summary

This 12.47 kV outdoor vacuum contactor controller system provides power switching for the PEP-II particle accelerator RF power supplies. The system receives 12.47 kV power through a loop feed configuration using 3/C 350MCM cable from the area substation. The vacuum contactor (15kV, 400A, 3-pole) serves as the main switching device, controlled by the Ross Engineering HQ3 driver unit which uses stored energy (capacitor-based) closing. Protection is provided by overcurrent relays (50-51) on all three phases plus neutral, an undervoltage relay (27), and a blocking relay (BR) that activates when fault current exceeds 2000A. The system includes local and remote control capability through MX (remote), TX (local trip), and OL (local control switch). Current transformers (CT 50/5) on each phase provide current measurement for protection and metering. The entire assembly is housed in a weatherproof NEMAT-rated metal enclosure mounted on a concrete pad, with door-in-door access and safety interlocks. The system feeds downstream to variable voltage transformers and HV power supplies that serve the accelerator RF systems.