# Technical Note: 12.47KV Outdoor Switchgear
Vacuum Contactor Electrical Schematic Diagram

Source Document: gp4397040201.pdf
Document Type: Technical Note – Circuit Schematic Analysis
Purpose: Detailed extraction of design information from circuit schematic for AI-assisted design reconstruction

────────────────────────────────────────────────────────────

# 1. Document Identification

## 1.1 Title Block Information

Title: 12.47KV OUTDR SWGR, VAC CNTOR – ELECTRICAL SCHEMATIC DIAGRAM

Drawing Number: GP-439-704-02-C1 (CAD redraw)

Original Drawing: GP-439-704-02 R0 (manual drawing, superseded)

Organization: Stanford Linear Accelerator Center (SLAC)

Affiliated: U.S. Department of Energy / Stanford University, Stanford, California

Project: Positron Electron Project 2 (PEP-II)

Engineer: A.A. Cheng

Approved by: William DQ (initials)

Scale: None (not to scale)

SLAC Release: V:\MDCAD\DocumentControl\Images\Incoming\SLAC\PEP2 VCC2.dgn.tif

Release date: 9/25/2006 12:06:00 PM

Proprietary: Data of Stanford University and/or U.S. Department of Energy

## 1.2 Revision History

Original: Manual drawing GP-439-704-02 R0

C1: Redrawn to CAD as shown and revised per as-built conditions (date: 09/25)

# 2. Circuit Overview

This is the detailed electrical schematic diagram for the 12.47 kV outdoor switchgear vacuum contactor system used in the PEP-II accelerator at SLAC. It provides the complete circuit logic for all control, protection, and power supply subsystems. The drawing is organized into functional blocks covering: overcurrent protection and ground trip, vacuum contactor open/close circuitry, energy storage closing, DC voltage sensing, internal HV and LV DC power supplies, and the interface to the RF power supply transformer. This is the most detailed schematic in the switchgear documentation set and is the primary reference for understanding circuit operation.

# 3. Functional Block Diagram (as shown on schematic)

## 3.1 Block Layout (Left to Right)

OVER CURRENT / GROUND TRIP: Overcurrent protection with 50-51 relays

OPEN CONT / VAC CONT TRIP CIRCUITRY: Opening/tripping logic

VAC CONT 'OPEN/CLOSE' CIRCUITRY: Vacuum contactor control logic

"CLOSE" IF READY INDICATOR CIRCUITRY: Ready-to-close verification

DC VOLTAGE CIRCUITRY: DC bus voltage monitoring

INDICATOR: Status indication circuits

INTERNAL HV DC POWER SUPPLY: High-voltage DC supply for energy storage

INTERNAL LV DC POWER SUPPLY: Low-voltage DC supply for control circuits

## 3.2 Additional Blocks

UNDER VOLTAGE (BLOCK 1) CIRCUITRY: Undervoltage detection and protection

FAST DROPOUT: Fast de-energization circuitry for rapid contactor opening

NEUTRAL connection: System neutral reference

VACUUM CONTACTOR/DRIVER CIRCUITRY: On switchgear control circuitry section

# 4. Detailed Component List

## 4.1 Relays and Control Devices

MX - Remote close relay (main command relay for closing sequence)

TX - Local tripping relay / Aux tripping relay (15, connected to TB1-17)

K1 - Main operating relay (controls stored energy application)

K2 - Ready relay (K2A, K2B contacts, indicates energy storage ready)

K3 - Current sensing relay (monitors holding coil current, Telemecanique type)

K4 - Control voltage interlock relay (HOT on TB1-1)

CR1 - Control relay 1 (part of door interlock/cap dump circuit)

CR2 - Control relay 2 (part of sensing/protection circuit)

BR - Blocking relay (activated by excessive fault current >2000A)

RR - Remote reset relay (3.2A rating)

TD1 - Time delay relay (Telemecanique auxiliary time delay)

## 4.2 Overcurrent Protection

50A - Phase A overcurrent relay

50B - Phase B overcurrent relay

50C - Phase C overcurrent relay

50N - Neutral overcurrent relay

51A, 51B, 51C, 51N - Time-overcurrent elements (combined 50-51 function)

CT200/5 - Current transformers, ratio 200:5, on each phase (H1/X1 connections)

## 4.3 Vacuum Contactor (Model HQ3)

S1A, S1B - Interlock switches (mechanically sealed-in position sensors)

S2 - Limit switch on contactor (TB2-S2, TB2-S2B - LIMIT indication)

S3A - Indicating switch (TB2-S3A - INDIC)

S3B - Indicating switch (TB2-S3B - INDIC)

L1 - Holding coil/solenoid (DC holding, drops out within 1 cycle)

L2 - Closing coil/solenoid (receives stored energy for closing, L2-22)

P - Vacuum contactor terminal (TB2-5, TB3-18)

Operating mechanism: Toggle-based with high closing force

## 4.4 Energy Storage and Power Supply Components

C1 - Closing energy storage capacitor (3500mF, 25W charge resistor)

C7 - DC bus filter capacitor (40,000mF, rated 40V)

Charging resistor: 10M ohm, 25W (for C7 slow charge)

Voltage sensor: Monitors +350 VDC on energy storage bus

D1 - Diode (in K1/K2 circuit path for energy storage)

6/10A fuse - DC power supply protection

50f, 100W resistor - Power supply load/bleeder

330K, 250K resistors - Voltage divider for sensing

1W, 2W resistors - Associated with MX circuit

R5 - Resistor in TB3 circuit

220 ohm, 50W resistor - Discharge/bleeder resistor for energy storage

10n capacitor (C1 area) - Snubber/filter capacitor

56K resistor - In MX/BB circuit

BB1, BB2 - Terminal/bus bar connections

## 4.5 Indicators and Status

NEON indicator - Ready status (neon lamp)

READY indicator - Shows K2 relay status (energy storage sufficient)

NOT READY indicator - Shows insufficient stored energy

OPEN/CLOSE indicators via S3A/S3B switch positions

Operations counter

## 4.6 External Equipment Interfaces

RFPS TRANSFORMER: RF Power Supply Transformer connection

MCO - Main contactor output (connected to TBD-3, TBD-4)

50/51 test block connections (A, B, C phases)

F200 fuses (3x) - Protection fuses for RFPS circuit

LOCKOUT RELAY - Connected to TB3-10, TB3-12 (MC5, MC7 contacts)

# 5. Terminal Block Assignments (Detailed)

## 5.1 TB1 - HCA Driver Box Terminal Block

TB1-1: K4 (HOT) - Control voltage interlock

TB1-2: Neutral / VAC CONT connection

TB1-4: Vacuum contactor Zo connection

TB1-6: Vacuum contactor connection

TB1-7: 51A, 51B, 51C, 51N relay power (multiple connections)

TB1-8: CR1/Door interlocks cap dump

TB1-9: Closing energy circuit (3500mF capacitor, 25W)

TB1-10: CR2/K1 circuit

TB1-11: MX/Remote close relay connection (MTL contactor)

TB1-12: K1 circuit

TB1-15: Door interlocks cap dump (shown with door closed)

TB1-17: TX/VAC CONT connection

TB1-18: MX/GRE circuit

TB1-19: CR2 connection

TB1-20: Internal HV DC power supply

TB1-21: CRI/30A fuse connection

## 5.2 TB2 - HQ3 Vacuum Contactor Terminal Block

TB2-1: Fast dropout / DC holding / 6A-600V

TB2-2: C7 capacitor (40,000mF) / R5 / TX circuit

TB2-3: Local ready / NEON

TB2-4: CR2/RR sensing circuit

TB2-5: P terminal / vacuum contactor

TB2-6: Voltage sensor connection

TB2-9: S2 limit switch

TB2-11: S2B limit switch

TB2-12: Local reset / PB

TB2-14: MTL contactor

TB2-S2: Limit indication

TB2-S2B: Limit indication

TB2-S3A: Open/close indication (INDIC)

TB2-S3B: Open/close indication (INDIC)

## 5.3 TB3 - Switchgear Terminal Block

TB3-5: 27 relay (AG circuit)

TB3-6: Closing energy relay (20G circuit)

TB3-7: R5 circuit

TB3-8: 10M/TBS circuit

TB3-9: MX/GRE / TX circuit (10 wire name)

TB3-10: BR/CR2 / lockout relay connection

TB3-11: BR circuit

TB3-12: 17 wire / lockout relay

TB3-13: CC/FF circuit

TB3-14: Internal LV DC power supply

TB3-15: RR / K4 circuit (CC connection)

TB3-16: BO / vacuum contactor

TB3-17: Vacuum contactor

TB3-18: P / vacuum contactor (DD)

TB3-20: BB1 / K4 connection

TB3-21: K1/CC1 / S1A / 6A-600V

TB3-22: 56K / BB2 / MX connection

TB3-24: CR2 / MTL connection

## 5.4 TB4 - Power/CT Terminal Block

TB4-6: Phase connections (21B, 22) for incoming line CTs

## 5.5 TBD - RFPS/External Terminal Block

TBD-1, TBD-2: External connections

TBD-3: MCO connection

TBD-4: MCO connection

TBD-5: External (AM circuit)

TBD-6: External connection

TBD-7: Oil pressure relief / overtemp

TBD-8: 86-L (BR) lockout relay external

TBD-9: RF power supply transformer

TBD-11: RF power supply transformer

# 6. Sequence of Operation (Verbatim from Drawing)

## 6.1 Energy Storage Closing – Vacuum Contactor/Driver Model #HQ3

The following sequence describes the complete closing and opening operation of the vacuum contactor system:

## 6.2 TO CLOSE

1. MX CLOSED TO START SEQUENCE OF CLOSING HV VACUUM CONTACTOR.

2. CURRENT SENSING RELAY TO CHECK VOLTAGE IN HOLDING COIL. CHECK K3 VOLTAGE IN CLOSING COIL.

3. WHEN FULL CURRENT IS REACHED IN HOLDING COIL, K3 CLOSES AND IF K2 READY RELAY IS CLOSED, WITH FULL ENERGY AVAILABLE AND HOLDING COIL IS MECHANICALLY SEALED-IN THUS ACTUATING INTERLOCK S1, K1 THEN CLOSES APPLYING STORED ENERGY TO CLOSING COIL L2. (BLOCK 1)

4. L2 SOLENOID THEN CLOSES TOGGLE WHICH CLOSES HV CONTACTS WITH HIGH CLOSING FORCE.

## 6.3 TO OPEN

5. MX OPENED TO START UPON SEQUENCE OF VACUUM CONTACTOR (OR TX, LOCAL OFF, OR INTERLOCKS OPEN). (IF BR BLOCKING RELAY CLOSED BY EXCESSIVE FAULT, MX AND TX LOCAL OFF ARE BYPASSED AND CONTACTOR CANNOT OPEN IMMEDIATELY EVEN IF AC IS LOST AND AS LONG AS BR STAYS CLOSED UNTIL CG DECAYS. WITH LOSS OF AC CONTROL VOLTAGE, CONTACTOR WILL HOLD IN FOR AT LEAST 170 MILLISECONDS BEFORE DROPPING OUT).

6. WHEN DC CURRENT IS SHUTOFF TO L1 HOLDING COIL, L1 HOLDING SOLENOID DROPS OUT WITHIN 1 CYCLE DROPPING TOGGLE BASE AND OPENING HV VACUUM CONTACTOR WHICH THEN CLEARS IN APPROXIMATELY 1/2 TO 1 CYCLE. (HV CONTACTS NOMINALLY AT THE FIRST CURRENT ZERO AFTER CONTACTS PART).

7. AS SOON AS L1 DROPS OUT AND OPENS HV VACUUM CONTACTS TOGGLE BREAKS AND RESETS L1 AND L2. THIS THEN ALLOWS RECLOSING, AFTER ENERGY STORAGE CLOSING CAPACITOR IS RECHARGED IN A FEW SECONDS TO A LEVEL SENSED BY THE DRIVER VOLTAGE SENSOR WHICH THEN CLOSES K2 READY RELAY.

8. READY INDICATOR THEN INDICATES WHETHER VOLTAGE ON ENERGY STORAGE CLOSING CAPACITOR IS SUFFICIENT FOR POSITIVE CLOSING AND ALSO ALLOWS CLOSING SEQUENCE TO START IF MX AND REMAINDER OF CLOSING CIRCUIT IS CLOSED AT RESET. ANTIPUMP RELAY MAY BE NECESSARY, HOWEVER, RECHARGE TIME REDUCES PUMPING RATE. USING TX IN A RESET CIRCUIT SUFFICES FOR POSITIVE ANTIPUMP.

9. DOOR INTERLOCKS ON THE ENERGY STORAGE DRIVER UNIT AUTOMATICALLY DISCHARGE CAPACITORS WHEN DRIVER DOOR IS OPENED. EXTERNAL TERMINALS ARE ALSO PROVIDED TO TEST OR DISCHARGE CAPACITORS WITHOUT OPENING DOOR.

## 6.4 CAUTION

AC MUST BE OFF BEFORE EXTERNAL DISCHARGE OF CAPACITORS IS DONE TO PREVENT BLOWING AC FUSES.

# 7. Protection System Details

## 7.1 Overcurrent Protection

Phase overcurrent (50-51 A, B, C): CT ratio 200/5, connected via test block

Neutral/ground overcurrent (50-51N): Separate neutral CT

Blocking relay (BR): Activated when fault current exceeds 2000A; prevents contactor opening during fault

Lockout relay: Connected to MC5, MC7 via TB3-10, TB3-12

## 7.2 Undervoltage Protection

27 relay: Undervoltage detection (Block 1 circuitry)

Connected to AG circuit (TB3-5)

Monitors incoming 12.47kV line voltage

## 7.3 DC Voltage Monitoring

Voltage sensor on +350 VDC energy storage bus

K2 ready relay indicates sufficient stored energy for closing

330K and 250K resistor divider for voltage sensing

Fast dropout circuitry: 6A-600V rated for rapid de-energization

## 7.4 Fault Ride-Through (BR Blocking Relay)

BR closes when fault current exceeds 2000 AMPS

While BR is closed: MX and TX local off commands are bypassed

Contactor maintains closed position even if AC is lost

Contactor holds for at least 170 ms before dropout (loss of AC control voltage)

Contactor opens only after CG (capacitor group) energy decays below holding level

# 8. Internal Power Supplies

## 8.1 Internal HV DC Power Supply

Supplies +350 VDC for energy storage capacitors

C1: Main energy storage capacitor (3500mF, charged through 25W resistor)

Voltage output monitored by voltage sensor circuit

Protected by 6/10A fuse

Feed-through resistors: 50f, 100W for controlled charging

Connected to TB1-20

## 8.2 Internal LV DC Power Supply

Supplies low-voltage DC for control relay operation

Connected to TB3-14

H 125VDC power bus for switchgear control

FU-A: 30A fuse protection

Powers door interlock circuits, relay coils, and indicator lamps

## 8.3 Fast Dropout Circuit

Provides rapid de-energization of holding coil

6A-600V rated components

DC holding coil dropout within 1 cycle

600V rated energy dissipation

# 9. Wire Names and Circuit Identifiers

Wire name assignments visible on drawing (column: WIRE NAME)

Numbered wire identifiers: 15, 17, 21, 22, 23, 28, etc.

Circuit identifiers: AG, BB, CC, CC1, DD, EE, FF, GG, HH, SS

Terminal-to-terminal wire tracing documented via TB1/TB2/TB3/TB4/TBD cross-references

# 10. Notes from Drawing

This drawing supersedes manual drawing GP-439-704-02 R0

TB1: Terminal block on HCA driver box

TB2: Terminal block on HQ3 vacuum contactor

TB3: Terminal block on switchgear

Reference: ID-308-801-06 PEP2, 12.47KV VAC CNTOR CONTROLLER, ELECTRICAL, CONN WIRING DIAG

# 11. Operating Principles Summary

This schematic represents the complete electrical control system for a 12.47 kV vacuum contactor used in the SLAC PEP-II accelerator's RF power distribution. The system operates on the stored-energy closing principle: a 3500mF capacitor bank is charged to approximately 350 VDC through an internal HV DC power supply. When a close command is initiated (MX relay), a sequence of checks verifies holding coil energization (K3 current sensing), adequate stored energy (K2 ready relay), and proper interlock status (S1). Upon verification, relay K1 connects the charged capacitor to closing coil L2, which actuates a toggle mechanism that closes the vacuum contactor's HV contacts with high force. The holding coil L1 then maintains the closed position using DC power from the internal supply. Opening requires interruption of the L1 holding coil current, which causes the toggle to release within approximately 1 power cycle. The system includes comprehensive protection: overcurrent relays (50-51) on all three phases and neutral with CT ratios of 200:5, undervoltage protection (27 relay), and a blocking relay (BR) that prevents premature opening during fault conditions exceeding 2000A. The 125VDC switchgear control bus provides power for the protection and control circuits, with safety interlocks on all access doors that automatically discharge energy storage capacitors when opened.