Utility Installation Requirements

1. RF Station (Future SSA Location)

Location: Corridor between the current SPEAR klystron building and the SPEAR ring (Building 122).
Purpose: House four Solid-State Amplifier (SSA) systems.

Utility Installation Requirements

- Electrical Service Estimate:

  - Four 500 kW services required.

  - Voltage: 480 V @ 601 A per service.

  - Code requirement: 20% over nominal current → Four 800 A breakers (one per system).

  - Sub-breakers per system: Preliminary estimate of 9 units (8 power units + 1 control unit).

    - Power units: 100 A each (Meltric offers 100 A and 150 A switch-rated connectors).

    - Control power: Supplied from existing 208 VAC transformers in the room.

- Low Conductivity Water (LCW) Estimate:

  - Formula: PW=fl/s⋅ρkg/l⋅cJkg⋅K⋅ΔTK, where

    - f water flow rate

    - ρ≈1 kg/l water density

    - c=4184 J/(kg⋅K) specific heat of water,

    - ΔT water temperature rise in Kelvin.

  - For 1 MW (10⁶ W)

    - with ΔT=1 K , f=63 gps=3783 gpm.

    - with ΔT=10 K , f=378.3 gpm.

  - Crosscheck with the recorded data: RF panel shows of klystron collector ΔT=13 K for 830 kW. The flow should be 0.83*378.3/1.3 = 242 gpm. Current LCW flow (per Eddie): ~200 gpm for the klystron, possibly slightly higher.

  - Note: Consult vendors to determine acceptable ΔT for devices, as it impacts reliability.

2. RF Test Station (Building 122)

Purpose: Testing SSA systems .
Status: Formerly a klystron station, currently used for storage, with existing utilities.

Utility Estimates

- Electrical Service Estimate:

  - 64 kW service required.

  - Voltage: 480 V @ 77 A.

  - Code requirement: 20% overhead → 100 A breaker.

  - Safety margin: Consider 150 A breaker.

  - Existing: Two 120/208 V panels (East and West).

- LCW Estimate:

  - For 64 kW:

    - LCW estimate: water flow  242 gpm for ΔT=1K

    - We need to cool the RF load as well as the SSA, which will increase about 50% of the rate.

  - Target: 50–80 gpm to maintain low temperate rise.

  - Existing plumbing (from 500 kW klystrons) should have sufficient flow.